## Sheet1
CaseId | CaseName | MemberCount | Category | CreatedFromDispatchId
CASE-0051 | Sushi s/c - located condensate pan overflowing. This unit utilizes a tiered condensate system with the discharge line and a heater. Found heater not operational , 120v present but not pulling amps. Heater measured OL with meter also. Need new heater Meat s/c #1 - Found evapoway pan with holes rotting from the sides. Interlock relay for pan also melted and burned up. Need to have new pan and DPDT relay ordered | 782 | Condensate Pan Failure | 9D67E30A-3A1E-48BD-8AE5-A2A3E9D4104D
CASE-0008 | All 4 bunker evaporators were iced over. Cleared the coils with hot water. Let fans run to dissipate the remaining water. Put system into defrost and verified amp draw on all heaters, checked out good. Put system back on line and let bunkers drop to temp. Found bunkers flooding back. Adjusted SH on all evaporators, cases are now balanced no longer flooding back and achieving set point. Leaked checked the store and found no leaks. | 565 | Coil Failure | 4CC8469F-378C-41DE-910A-F9F1C29E4248
CASE-0001 | No technical fault identified in dispatch notes. | 513 | No Technical Fault | 2EE8FED6-799B-42C9-9FEB-C9E981929811
CASE-0622 | Found MT2 Compressor locked out on oil fail. Reset compressor and observed oil system. Found very poor oil migration, due to closed ball valve on oil reservoir vent line to vessel. Opened line to allow reservoir to maintain vessel pressure and proper differential. Found HSBO2 oil level sensor triggering falsely due to poor connection between mechanical and electronic base. Removed base and cleaned pin to make connection good again. MT1 Compressor also tripping off on oil failure for two reasons; Reason #1- HSBO2 oil level sensor was intermittently indicating no level with green LED’s, despite full oil in sump sight glass. Pumped out compressor and removed and replaced HSBO2 mechanical sensor with spare found on site. Tested old sensor in oil to prove failure. Reason #2- the rack oil level is too low, as the compressor tripped oil failure again due to a true low oil level inside the compressor, when the reservoir and the compressor make a call for an oil fill at the same time. One gallon of RL85HB oil will need to be added to the rack. | 476 | Oil System Failure | 55A252DC-40D3-4A50-A08E-35DB30137329
CASE-0344 | compressor1 suction Schrader valve and hot gas Schrader valve were leaking I replaced the Schrader valves to stop the leak | 453 | Refrigerant Leak | 1EE6DFF7-207E-4D68-A27C-8FAC24E7E342
CASE-0193 | See temp came down and out of alarm monitoring while checking components noticed the sensor for that case has 7 deg offset on it and was all over the place on temp range I replaced sensor and it was more steady no further alarms while on site | 433 | Sensor Failure | A1EB4951-86D7-4F4A-B207-B79F35E3E2AC
CASE-0103 | Blower motor belts was broken. There was a new belt in the unit, replaced it and got unit running. Checked out main unit and found 2 bad condenser fan motors. Also circuit 2 is low on refrigerant. Checked out office unit and it is low on refrigerant. 1 of the make-up air units has a condenser low on refrigerant and another one with a bad condenser fan motor. Checked out exhaust fan not working and found bad connection on transformer feeding power to motor driver. Fixed connection and exhaust fan is working properly now. | 399 | Condenser Fan Motor Failure | D92C011A-ACAA-49C4-9113-E07F92B75DD3
CASE-0136 | The warm temps they are seeing is lining up with defrost schedule. | 391 | Defrost Cycle Issue | B0D2F4B7-9899-404F-A66E-4900D76C119F
CASE-0020 | Found issue was a clogged drain line, using nitrogen and a vacuum to clear the clogged drain line. | 264 | Drain Blockage | B03012DB-0965-473F-973A-A001E89390EE
CASE-0178 | Found blower motor bad motor had 24 volt call and 230volt power going to motor but motor not spinning | 260 | Fan Motor Failure | A5293C54-A455-4701-8E2B-F3CC74CC5A27
CASE-0084 | No current draw on rear defrost heater with 220V present. Ohm test across heater with leads removed open. Heater has failed. Cable for Carel control not working. Will need to have a tech replace cable. | 256 | Heater Failure | CC3A5B60-9C2D-4479-B5DF-8DE67D9CC6BE
CASE-0057 | I found that the neutral wire from the switch to the board was melted and no longer making contact. | 219 | Electrical Wiring | 66CAA75C-4E3A-4D43-86B7-E75255048CEF
CASE-0286 | Found far right fan on A5b had badly bent blade and excessive ice buildup, especially on section with damaged fan blade. Removed failed blade, installed new. Confirmed new blade running correctly. | 212 | Fan Motor Failure | 7461A872-97D9-4C7D-8953-B97F7B4F5B4E
CASE-0016 | Found rack off on high pressure. Cond dans running but dirty condenser. Cleaned cottonwood off condenser and did a controlled start up of rack. Watched suction pressure hit setpoint and watched discharge pressures. | 183 | Condenser Blockage | A676B6F1-5D8B-41E9-818E-83869001130F
CASE-0500 | Found stater on EEV connection corroded and EEV not completely closing when at 0%. Found suction sensor not insulated and fan with bad bearings making a very loud noise. Insulated sensor and replaced motor and verified all 3 case now maintaining set point temperature. Found EEV sticking open. Found large leak on liquid line service valve pulled vacuum and could not achieve vacuum, pressure tested system and found suction filter drier leaking on shell, relived suction drier. Recovered contaminated refrigerant. Verified all product is pulled in cases and will leave vacuum overnight. Found a leak and a bad dual pressure control. Found large leak on liquid line service valve pulled vacuum and could not achieve vacuum, pressure tested system and found suction filter drier leaking on shell, relived suction drier. Recovered contaminated refrigerant. | 179 | Refrigerant Leak | 079C4761-0326-4917-A377-ED9F6B3BE931
CASE-0030 | Found left side 2 doors evap coil iced up, set Copeland control to manual defrost, defrost heaters are operating, found 3 of 4 doors with door gaskets folded in on the top right to midway down on all 3 doors causing doors not to seal properly and further left door, door opener plate causing door to not close all the way, leak checked case and found no refrigerant leaks, let case to deice with defrost heaters since cases drain are plumbed to a condensate pump and manual deicing would flood digital work area, found spare door gaskets on site and replace all 4 door gaskets with new, evap still has some ice, put case back into manual defrost, monitor defrost, remove defrost, minimal ice on evap, had doors remain open with evap fans operating to melt remaining ice off coil, had digital TL to leave doors open for a few hours to melt remaining ice, spoke to SM Mark and that I will return in 3 hours to inspect ice. Return to store, inspect ice, no ice in evap, turned on circuit, monitor temps, starting case temp at 75 degrees, temp at 32 degrees with a downward trend, shut off case at breaker, did another leak check, no leaks found, turned on case, all is in proper operation, notified and checked out with Coach Gary. | 164 | Door Seal Failure | 4E656EA4-EB5C-41C8-A982-40AAD95CCC30
CASE-0248 | I found both the left side and the right side gaskets are damaged and not sealing properly. The right side was missing a small piece of the white plastic. | 133 | Gasket Failure | AA4D57A2-8C24-4AAF-96BD-2E584B23FA3B
CASE-0138 | Based on current operating conditions and temperature history, it is possible that the TXV cartridge is compromised, the inlet cone filter within the valve is partially restricted, or the distributor/orifice downstream of the valve contains debris. | 126 | TXV Failure | C8B30B2E-E6E6-4181-9E10-0CE111957225
CASE-0053 | Found contactor T2 contacts blown. Powered off unit removed and replaced contactor. Restarted unit compressor turned on and case dropped temp immediately. Unit online job completed | 117 | Contactor Failure | B35419D2-56B3-432F-8CF6-7D56080F0766
CASE-0336 | I did confirm that the breaker for system 4 was tripped , also the breaker for compressor 1 was tripped as well. I did try to reset both but they never stayed on. They still tripped. I shut down the rack to check the breakers and confirmed both were completely bad. | 117 | Breaker Failure | 7A367E3F-A27A-4D44-AC51-35517C6AB756
CASE-0152 | Upon speaking to management, they informed me the store underwent a power outage. This work order is to confirm all communications and rack systems are back online. Located roof hatch and found racks on roof. Confirmed racks are online and operating. Called Walmart digital assets and confirmed all communications and temps with operator. All communications are back with no temperature issues or alarm issues. Work is complete, informed management and checked out. | 95 | No Technical Fault | 20AC6979-FA3C-434C-9FB5-BACE908A1B5E
CASE-0005 | Found no other issues. | 87 | No Technical Fault | 248057F2-7A6E-4265-8C2A-0DFFC812EC8B
CASE-0232 | noticed compressors were locked out due to condenser coils being clogged with dust | 83 | Coil Failure | BC6BAE6C-AC4D-45EF-94BF-938A70BA03AC
CASE-0211 | No leaks were found on follow up All valves, caps and connections checked No leaks found On rack C No trace of leaks found in motor room | 76 | No Technical Fault | 872F59E7-87F0-4BDE-A943-A0F669BBC08B
CASE-0150 | Found a fan unplugged. | 73 |  | 608E8801-DAAC-4123-881E-4BD25B71D564
CASE-0047 | Got hit on Loop C1 suction header Schrader, also had a missing brass cap. | 72 | Refrigerant Leak | 6D38AC9E-B592-4E2A-BB62-36375300DB2D
CASE-0159 | Found blown control fuse due to Maine store power outage. | 71 | Control Fuse Failure | 8FBAE147-AD3C-4B97-B757-E35C5CAF0D30
CASE-0035 | Solenoid magnet came off of liquid line solenoid electricians never wired the solenoid valve up | 67 | Solenoid Failure | 4724282F-6687-4294-B674-71682F75AFA1
CASE-0221 | A faulty low pressure switch was found on a Hussmann Coil. | 67 | Switch Failure | 6B9AF06F-F285-4BCE-91DD-3A179AB505A8
CASE-0021 | Center door the upper hinge/closer assembly is damaged and the spring pops out of place when attempting to adjust closing force. Need to replace upper hinge on center door. | 64 | Hinge Failure | 1BFD3A27-9EF5-478F-8E63-CF6483E9DE6D
CASE-0184 | Rack M3 is leaking at plug ontop of receiver, pumped out receiver and isolate, pumped reminding pressure into rack M1, removed plug and added teflon tape and thread sealant, put receiver into a vacuum l, leak checked plug and added 125# and checked operations all is normal | 62 | Refrigerant Leak | A2DC6291-6A0D-45F0-B28F-315FB98D3C93
CASE-0050 | Arrived on site found no power going to package rack unit on roof, search store for panel for rack but finally located it in a hallway in back of store. Rack B breaker switched off not tripped no panel door. Look like someone got caught on it and switched it off by accident store is under going construction and hallways are close. | 57 | Electrical Wiring | 0DF34F46-6A29-4043-86FD-6F962F325369
CASE-0025 | I traced out and found rack 3 compressor 3 grounded and passing through breaker. I isolated the compressor and electrician reset breaker. | 56 | Compressor Failure | 3375FF87-A05C-470F-96A2-A09F0AFE768C
CASE-0062 | Discovered the 2nd door from left of frame had a bad torque rod that lost its tension. Removed old torque rod and installed new rod, also installed the new torque master. Discovered the nut from torque rod that sits into torque master had snapped and failed. | 56 | Torque Rod Failure | A2FB28EC-B28A-460B-8667-B25492D8DD06
CASE-0046 | Contactor was all burnt up. Reset switch was not working properly was able to reset oil control. | 54 | Contactor Failure | 2E283B99-D58E-4DFF-BB01-60B54959951C
CASE-0339 | Check and found that condenser had the screen over lap and choking Air Supply. So took off and blew out condenser then went to check set point found controller was not working properly and glitching. | 53 | Controller Failure | 75F7F28D-D60B-4E6D-B411-747A91E99398
CASE-0088 | Inspected RTU-4 and found the blower drive sheave severely damaged. Further inspection revealed failed bearings, which caused excessive wear and damage to the blower wheel hub and shaft assembly. Due to the extent of the mechanical damage, the unit cannot be safely operated at this time. | 50 | Fan Motor Failure | 2898A35F-92C5-4155-8D83-5EE1B0CA9E70
CASE-0056 | Found Rack data not matching e3 data. This is a fresh meet MDU. Graphs for defrost not matching e3 schedule. Looks like program wasn’t pushed or didn’t go through when pushed. Pushed from e3 to controller. Got call back from Wyatt at 02:51pm and he told me it previously had 4 defrosts a day and he changed it this morning around 10pm to 6 but didn’t write it to the controllers. | 49 | Control Board Failure | B523FD5F-973B-4DA1-AA03-58BA09D769BC
CASE-0272 | Found block of ice on evaporator, also found suction line and compressor in outside unit are iced severely. Coil is separated from duct allowing air to escape. | 43 | Coil Failure | B1083338-92A6-40B7-8CC0-DCD4C6297CCF
CASE-0651 | Found the dairy air curtain door with very little air flow. Used the scissor lift to access the blower compartment and found the blower motor belt worn/loose. Replaced the belt and left a new spare belt inside the unit. Inspected the coil and found the coil completely covered with lint/dirt buildup. Brushed off the lint covering the face of the coil. | 42 | Fan Motor Failure | B15E143E-2511-4AB3-8A0D-46AA17872552
CASE-0061 | Found a Dehumidifier fan under the case, the wire to the fan was in the path of the spindle. So as the fan is spinning it would hit the wire. | 40 | Fan Motor Failure | 23A4FB93-12C3-413F-930B-3C364BEDAADB
CASE-0019 | Found high suction pressure. Checked rooftop unit found unit compressor not running. Found contactor engaged. Checked voltage and fuses show to be bad. Picked up replacement fuses. Returned back installed. System began to run. Found heavy floodback on compressor could be cause of compressor fuses blowing due to compressor filled with liquid. Ran a defrost to check operations, found defrost termination sensor reading inaccurate causing box to only run its set minimum 10 minute defrost. Noticed heavy frost starting at txv body, removed txv screen, screen completely clogged. Torched txv body, to clear any logged dirt inside. While Box pulled down, verified case temp sensor with ice water-good. NOT A CALLBACK, box started high temping around same time term sensor started to fail. Box in negative temps on departure, freezer has high SH and experiencing a hot pulldown as box hasn’t been below zero in a few days. | 40 | Compressor Failure | A7C07F77-04F9-49B2-8A1A-CAE6D3E2DDD6
CASE-0158 | Found no differential at oil reservoir. Found oil moving slow through oil line sight glass showing float issues. Found oil float really dirty and with gasket torn apart. Installed new float and gasket. | 38 | Oil Float Failure | B3C53BCC-CF43-44A2-8088-6F0CD8A2BF59
CASE-0074 | I tightened down the terminations on the boards and trace back the wiring confirming that there were no tears. | 38 | Electrical Wiring | 4529A3CE-A2C9-48AD-933B-77541C095138
CASE-0018 | Did discover the leak sensor had been unplugged from box, plugged in and roughly 15 secs after the alarm shut off. | 37 | Sensor Failure | C8E5C013-91F2-4E22-B16C-93869F26436C
CASE-0179 | Remove power and wire both compressors back in. Start unit and verify case dropped down to proper temp and cycle both compressors off, check good. Cycle system through defrost and verified both compressors de energized and went through proper defrost, check good. | 37 | Compressor Failure | 78F51519-9A57-4BCA-8DE3-6599ADF50097
CASE-0089 | During inspection, found the run capacitor on RTU-1 weak and out of tolerance. Capacitor is rated for 7.5 MFD and tested at 5.1 MFD, which is below the acceptable range and may affect motor performance and reliability. | 36 | Capacitor Failure | 65D0E8BE-2FF8-4023-967E-2CDF3003846F
CASE-0282 | Checked EMS and Found: OPUS MAG on MTD shows no connection. rack in Comm loss. Store in possible power putage. | 35 | Communication Failure | AEC79D69-6045-4F47-A83F-8AADC7FFF34D
CASE-0123 | Found control wiring to compressor E1 unplugged due to vibration. | 34 | Electrical Wiring | 1BF2E8FF-C656-42FA-8C57-7AE5DE507F02
CASE-0042 | I checked the MDU of the meat and they had absorbent socks, I asked them to remove the products from that area, I checked the drain and it was a little dirty and with water, clean the drains and the buffer box too, clean the area and leave clean, wait for a while checking for some other leak and everything is fine. | 34 | Drain Blockage | 94C80828-AE13-4A45-A1BF-6E6610C6987D
CASE-0243 | Tested txv and it’s not feeding properly. Need to replace liquid line drier too. Used torches to weld off the bad TXV and liquid line drier. Welded on new TXV and new liquid line drier. | 33 | TXV Failure | F315DC8F-11E5-4AC5-A127-0F90C1ECABD1
CASE-0097 | Found TXV at high superheat. | 33 | TXV Failure | F814B784-C872-48DE-B0C0-E2C2AB06E531
CASE-0486 | Found walk in meat door handle not operating properly due to a old spring, making it hard to push open from the inside, took the push rod and Door handle off attempting to make repairs with no success. Will need to send this to office to order parts. Will need a new door latch for the outside and new push rod for the inside. Need to order a new door handle for the meat walk in box, Kason K-55 door handle And a Kason Push rod/inside release.(part # 0486)(Will need two of these) the other walk in door in the meat department is broken as well. | 32 | Door Mechanism Failure | 40F528B8-5D5C-4DBD-AEA7-C8304ABC9159
CASE-0227 | Found (7) suction line sets with old damaged insulation that needs to be replaced. | 32 | Insulation Failure | 8B208141-6F35-4B9F-9BF4-09DCC6D866A5
CASE-0240 | Found unit was not cooling due to a frozen evaporator. Thawed the coil out and checked pressures. Found filter was clogged up. Pulled filter and checked again. Temp split is slightly high due to it being on a concentric duct system. System cooling well at this time. Check IN Date: 6/3/2026 3:30:35 PM. CLASSROOM Preschool / Air Conditioning / Heating / HVAC Unit/Furnace / Not Working / Is request in response to a licensing write up?: Yes / Air is not working again. still no air filter in it Barry was suppose to put one in and has not When they came out to fix it they said it was froze up due to dirty filter that they took out. The room is reading 75 and getting hotter. I will have to shut it down if not fixed that is 24 children and families that will not be able to attend tomorrow. Checked in with Manager checked thermostat thermostat a little too high checked RTU for RTU for evaporator was frozen up deiced evaporator drain was clogged and coil was clogged with dust. Cleaned off evaporator coil and cleared drain checked airflow airflow good everything tipping correctly notified customer to put in filters ASAP | 30 | Coil Failure | 642EB2AB-7BAE-49E5-909E-8AC19524A1E4
CASE-0083 | Checked door switch control board and it is bad. Board has power to it, but no LEDs are lit and it is not breaking fan power when the door is open. | 29 | Control Board Failure | 6E479395-575C-4EFD-A718-3009F797230A
CASE-0166 | I found condensate pump unplugged | 29 | Condensate Pump Failure | C8656005-F7FF-4AE5-AC66-950ED645F02D
CASE-0145 | Found leak at txv between txv and distributor. Found heat reclaim solenoid shorted replaced solenoid and put into service. Heat reclaim tank 2 has been changed out and need to be repiped to heat reclaim in rack 6. | 29 | Solenoid Failure | C029E1BD-30E1-4D4B-849F-45E978843EEF
CASE-0410 | I arrived at the store and consulted with the manager. I proceeded to identify the equipment and began the diagnostic process, finding the fans working with good airflow and no ice buildup. I checked the rack and found the temperature close to the set point. No alarms were detected. I performed monitoring, and the temperature dropped further, with no further issues found. | 28 | No Technical Fault | A18A2D4D-128A-4BE5-B687-46B1D96D2FC1
CASE-0096 | Glycol is leaking through overflow line due to Hoffman valve bleeding by. | 26 | Valve Failure | 48390F64-2D17-41FA-A00F-576107A1E480
CASE-0039 | discharge pressure jumped up to 1275psi at 12:40pm and came back down, fans running on gas cooler, water not calling for at the time, rack is in transcritical, discharge at 1075psi, all cases at temp, rack never tripped off | 26 | Refrigerant Leak | AED1F0E6-5FEC-423E-A4E3-66F47D4436CA
CASE-0777 | Both doors are not closing properly. First door is a mueller swinging door. Contacted mueller tech support to find out how to adjust tension rod. Loosened u bolt. Centered door where it needs to close. Loosened set screw. Tightened u bolt. Tightened set screw. Had to redo multiple times in order for door to closes properly. Door is now closing properly. Other door had a torque master. Adjusted torque master and door is now closing properly. | 26 | Mechanical Adjustment | AB4042AB-5E47-42B5-AFE7-96A6D1D70F5B
CASE-0040 | Found e7 frozen crab case has right side door track melted. Right side still hot. Frame heater ran with case fans which ties into MT case. | 25 | Frame Heater Failure | 98CB6C16-9AE7-4B26-A6B1-4776978C311F
CASE-0010 | Traced back to loose Ethernet connection. Re secured and started controller up. | 25 | Ethernet Connection Failure | 40222E32-EFA3-4C92-A89B-759D0CF0E41C
CASE-0323 | Traced out and found current sensing relay intermittently opening even when light shows closed. | 25 | Current Sensing Relay Failure | 04901860-E83B-4C2A-8D85-5C738F6E6159
CASE-0156 | Leak check store located leak on super hose for three-way valve for hot water reclaim, replace super hose and verified leak was repaired. | 25 | Refrigerant Leak | EF2110E7-5BC6-4C0E-B0EC-29E0A7848673
CASE-0144 | Found that the cables to the transducers were swapped. Corrected the cables and the return began reading but supply continued to read none. Checked the plug for the transducer and there was some corrosion. Replaced the cable with one that was on site. While replacing the cable noticed that the supply wire was connected to the 12vdc instead of 5. Corrected the supply voltage to the transducer with the new cable but it was still reading None. Changed the board and point which also did not work. Removed the transducer to inspect it, there was no debris inside the transducer or the angle valve. Replaced the transducer with the one that was previously in it and it’s working properly. | 25 | Transducer Failure | 7261A172-139E-40DF-AE7A-3BBE48B61546
CASE-0264 | Condenser has no dust on surface but is restricted. Condenser coil is 6-8” thick so very hard to get all the way through. Washed until clean water was coming out and water going all the way through coil. | 24 | Coil Failure | F245CDEF-2F18-4658-8B3F-BDBCEAD6EC37
CASE-0087 | To checked on the receiver pressure regulator valve. It needs replace | 24 |  | 758B72E6-AFBB-4D6D-A66D-5DD4466D585D
CASE-0033 | Looked under case and found condensation buildup. | 24 | Condensation Buildup | 5C65F0A8-6E36-4B9D-B8DE-9578B294D727
CASE-0085 | Found one dead motor on full side, one dead motor & broken blade on split side. One split side motor was running but, the blade was broken from the motor mount snapping. I found the split valve stuck shut. I was able to free up split valve by tapping the back of it. | 24 | Valve Failure | 46257230-FE73-44B0-9D47-A0A4BC3FFF57
CASE-0559 | The oil filter on the rack needs to be changed. The liquid line drier cores need to be changed. | 23 | Filter Failure | FD10A650-78BC-456B-B157-E1D907FEED0D
CASE-0556 | Found oil on rack a comp 1 rotor lock, looks like gasket was supposed to be replaced on ref PM, rack at 5-8% | 23 | Refrigerant Leak | A13811A5-6E05-4E87-8112-A980C4E57910
CASE-0164 | Found low level alarm on condenser refrigerant level. No leaks found. Will have to submit quote for further investigation on sensors and level control. | 23 | Sensor Failure | E89641DD-8027-4EB0-A895-ED2E59A944A6
CASE-0073 | Compressor A3L, farthest one on the left. Compressor is blowing by and will need to be replaced. | 23 | Compressor Failure | 0F4F64FD-7838-46E2-AFFA-BE579E87D436
CASE-0017 | After restoring power alarms did not come back, if this happens again in the near future the board will need to be replaced. | 23 | Control Board Failure | 944F6C6B-5155-4936-9402-20F43F710168
CASE-0167 | Suction transducer was also replaced on another call. When transducer goes bad compressors will continue to run past set point causing drop in suction temp and pressure which would also cause low super heat. | 22 | Sensor Failure | 57CF3F2A-8996-4B37-AEEF-8E499549A9F8
CASE-0298 | All six lights were bad. Found 26 lights missing or not operating correctly across all 8 wet produce cases. | 22 | Light Failure | 3C98143A-1D30-4913-B85F-175E1795324E
CASE-0514 | Found walk-in cooler with iced up coil. Shut off unit and deiced. Once fully deiced. Turned unit back on and found low charge. Leak search and found leak at receiver service valve. Tightened packing nut and caps to stop leak. Added 5lbs of r448a. Verified operations of unit and watched it come down to temp. Found evap coil frozen. Thawed coil and watched unit down to temp. Unit takes a long time to pump down and during defrost unit trips on high head before pumping down. Will need to clean txv and replace liquid drier then verify equipment operations. Found coil starting to ice up again. De ice coil and check defrost. Pressure is getting too high during defrost after initial pump down. Shut down compressor and performed non condensables test and found non condensables present. Would recommend changing condenser filter while system is open, Reclaiming all refrigerant and recharging with new. | 22 | Refrigerant Leak | E1A3C3E9-6B48-4BD3-8B29-E5E40F485AFD
CASE-0488 | I arrived at the store and consulted with the manager. I proceeded to identify the unit, which had fans running but the compressor was off. I began the diagnosis and found the Carell control unit damaged. The display indicated that the refrigeration was working, but there was no signal. I went to several supply stores but couldn't find a replacement, so I adapted a Dixell control unit. DNI ,After the adaptation, the magnetic contactor was found to be damaged. I returned to the supply store, and it was installed and restarted. The temperature began to decrease, the setpoint was adjusted, and it is now working correctly. | 22 | Control Board Failure | 1D1A5994-DEE6-45BF-87D1-027421BC3730
CASE-0835 | Found unit completely off so I started checking for power and found no power going to the unit. After looking around the unit more found that it was unplugged so I plugged it back in and the unit started running again and saw temps start dropping. | 22 | Electrical Wiring | 5A6D6350-7A75-4BA5-8995-799872798179
CASE-0090 | Found water leaking from the tower water pump. The water pump is in very poor condition, with rust and mineral buildup present. Due to the condition of the pump it needs to be replaced to fix leak. | 22 | Pump Failure | A89D5823-7C63-4FEF-92C6-67AE6C7282FF
CASE-0091 | Located case with no air flow and excessive dew around air discharge venting. All open air cases in area also have excessive dew build up. Shut off refrigeration and proceeded to E2; checked store humidity and found it at 67%, cases are designed to work at 55% or lower humidity. Excessive humidity will cause all open air cases to build up on frost and potentially restrict air flow. | 21 | Drain Blockage | C8ED60F6-ECFF-4650-A745-BE262729501B
CASE-0068 | All the controllers are randomly dropping out. | 21 | Control Board Failure | A3C6BDEA-E21F-490E-A7E7-E7A2C0B3F524
CASE-0858 | After diagnosing the unit I found the compressor on circuit 2 is grounded and needs to be replaced along with the filter drier and contactor. While doing this I found that circuit isn’t operating properly and is low on charge. | 21 | Compressor Failure | 6C0348E5-4061-4792-BF8E-9AFB5ACFBE26
CASE-0389 | Traced power wire back to electrical cabin and found delay relay malfunctioning dropping out when load is present, called traulsen to see if I can bypass delay relay and they said no it will void warranty, (bypassed relay to check compressor and it is working ok) unit is under warranty and they will send me new relay for repair (ETA is Friday) turned unit off to prevent any issues (parts are under warranty) | 20 | Delay Relay Failure | E1D0D5B0-50B8-4463-90FF-857E9F3EA17C
CASE-0330 | Located asset(s) listed on WO. Had product removed from lower section D05a and found cover over Right evaporator had slide down uncovering 2” on top of evaporator coil. Repositioned cover and also noticed the fan shroud had come loose from evaporator (design issue). Clips holding fan shroud against coil had come off. Bought some binder clips to secure fan shroud. Also found the fan shroud pulled away from Left evaporator on asset D-05c. Used binder clips to secure. | 20 | Fan Shroud Failure | 2ABB828B-3986-434B-9308-078905C7F52C
CASE-0454 | Found heater high temp limit klixon is stuck open. | 20 | Klixon Failure | 5C495EA7-DC9D-41E9-ACB3-333F2CF21F71
CASE-0168 | Ran cooling test with FMOC, Pressures are all operating within normal range Checked temps at vent and 68* supply air Setpoint in unit operating at 74* Cut in 76* Need to change setpoint. | 20 | No Technical Fault | 0CCB2964-45B8-4FF0-83B6-146CBDF534C2
CASE-0437 | I then inspected the sensor and found it to be severely damaged and corroded. To prevent additional false alarms, I disconnected the sensor. Further inspection revealed that the leak detector silencer was also damaged and will require replacement. | 20 | Sensor Failure | F4632C7A-4AFA-450B-9E6E-3D6FE0FEE20F
CASE-0201 | Found TXV adjusted too far open. I replaced the power head and cartridge of the TXV. | 19 | TXV Failure | 20F0CFF0-3B28-43B7-BEBD-F3C1CC16629A
CASE-0570 | Call was for the meat wall freezing product. Got roof access and found 2/3 cases running at 30 degrees with a 30 degree setpoint and the 3rd case running at 26 degrees with a 26 degree setpoint. Called RAM team and got the setpoint raised to 30 degrees to match all other cases. Case is maintaining 30 degrees and product is no longer freezing. | 19 | Setpoint Mismatch | 997D3829-79BA-417C-BA59-CB34216634DC
CASE-0115 | Found the thermostat is not working and holding the unit off will pick up a new | 19 | Control Board Failure | 8E62606E-2012-4519-86BF-03A41A570E9E
CASE-0293 | Found bad transformer. | 19 | Transformer Failure | C66EFE1D-22B9-4E1E-938F-CA1E1034AC9D
CASE-0197 | I discovered that all refrigeration units were down. After accessing the equipment room, I observed the head pressure was at 300 psi, with all compressors tripping due to high head. I began diagnostics and identified that the cooling tower water pump was not running, caused by a blown fuse. | 18 | Pump Failure | 83DBB25B-D899-464C-99EB-2B36A74CF477
CASE-0560 | The disconnect switch on the electrical panel was tripped. I reset it, and it started working, lowering the temperature to the set point. The disconnect switch tripped again. There was a smell of burning plastic, and the disconnect switch was hot. | 18 | Electrical Wiring | 24CEA035-3740-4AA6-A5E5-D8DBDEA0AB89
CASE-0063 | The liquid line ball valve was shut off. | 18 | Valve Failure | 493582C8-596B-46B5-95C3-EDDAE0AABDF4
CASE-0416 | I went up to the MTB chillers and found chiller B1 off on low suction and B3 off on flow proof failure. I went to B3 and checked to see if it had glycol at its highest point and it did. I made sure nothing was blocking it or valved off then I rest the unit. The unit came on and both pumps ran and the flow sensor was showing flow and the gauge showed it had pressure. I noticed a compressor cover blocking the condenser fan which was an issue. Once I removed it I reset the chiller and it came on and began to run and cool. | 18 | Fan Motor Failure | EDBCB792-C08C-4904-AED1-7EF5E0CC8F9E
CASE-0399 | Found big rub through on discharge line going into vibration eliminator. Cut out bad piece brazed in new one. | 17 | Refrigerant Leak | 1E0CA20B-453A-4979-BECB-C9F927D90C79
CASE-0163 | Case was being worked on earlier today. Case is fully operational at this time. | 17 | No Technical Fault | 9FC0910E-1F02-4F80-8148-CA9C6222BB67
CASE-0270 | Found Compressor 2 and Compressor 4 showing “No Proofing” alarms; however, both compressors were running normally. Verified current draw and confirmed the proofing circuits were operating correctly. | 17 | Control Board Failure | A2D2AD81-B70D-4112-B4C0-78546CC8FEE5
CASE-0529 | Compressor was tripping on low pressure. Sight glasses flashing. No leaks were found. Added 2 pounds of Freon into system. Sight glass was no longer flashing and compressor was no longer tripping on low pressure. | 17 | Refrigerant Leak | CA780827-94EA-4873-BE0C-F84E5D1F3A90
CASE-0642 | Found the compressor running but not pumping, with the suction line hot and sitting at 140 psi; the unit slightly low on refrigerant, so I added charge, thoroughly washed the coil to restore proper heat transfer, and adjusted the low-pressure switch to prevent short-cycling on pump-down; the unit is now running smoothly and holding properly. | 17 | Compressor Failure | EC5CCD06-6CD5-4820-87AE-68374D7F212D
CASE-0013 | Alarms most likely caused by a power flicker. | 17 | Power Flicker | B8551A74-1973-4137-9E24-CA130A7AAE0B
CASE-0558 | Looked at door handle and it seems like the push rod from inside the freezer is frozen. Removed both sides of the handle and saw ice buildup inside the door. | 17 | Drain Blockage | 4AA6F7D8-A45A-4C2A-866A-D5A81E2F5C21
CASE-0352 | Found unit off on smoke detector. Cleaned smoke detector and reset. Ac came back on, monitored and running good. | 16 | Sensor Failure | E447B7B9-5BB0-45F5-AD9F-594617CE6A02
CASE-0310 | Drain pump float switch was sticking. | 16 | Drain Blockage | 2747D888-95DC-46E4-9C23-6A62DD488A8F
CASE-0228 | He Jed operations and found that the honeycombs are plugged. Cleaned honeycombs and temps dropped from 50 to 35. Housekeeping issue. | 16 | Drain Blockage | FCF8FD1B-C366-4B1D-997F-1A40CBA3EE59
CASE-0093 | Replace failed Compressor C4 | 16 | Compressor Failure | 8373D5CC-2D0E-4B2D-A3D4-046A75DAA485
CASE-0640 | Case had strong airflow but the case digital thermometer reading was 40* while my digital thermometer and case dixell was reading 26*. | 16 | Sensor Failure | 8784C3F2-CD00-4127-BEE8-D349994CCBDF
CASE-0037 | Compressor was off on LP. LP needs to be replaced. Tapped on it with wrench. Compressor came on. And ran. Noticed a clear sight glass on liquid line. We need to return and replace LP control. | 16 | Control Board Failure | B21BBE16-45D1-477D-BA89-20CFA1F64ACA
CASE-0455 | Fan motor was not properly plugged in | 15 | Electrical Wiring | 49F0270A-50E8-4090-AD03-7F4CB5AAA113
CASE-0191 | Check power at relay output board and had no power present. | 15 | Control Board Failure | ED6B2733-269F-48D6-999C-11A663FFDE39
CASE-0402 | Found sticking hot gas valve. Will rebuild valve next day | 15 | Valve Failure | 957A4EE9-CCC0-4225-B1B3-07340DF57320
CASE-0079 | Found case at 40*F running warm due to high EPR setting. | 15 | Control Board Failure | 9128B2DD-5B23-4148-8816-76EF8B2BCC0A
CASE-0413 | Unit operating as designed. | 14 | No Technical Fault | 835E048D-0BD5-4E12-A6E8-D350DB3CAF4E
CASE-0414 | Found alarms for phase loss. Checked phase lose monitor all show to be proper voltage. Reset unit. Compressors began to run. | 14 | Phase Loss | 519C922D-5FFE-41D6-846D-3647860C12EC
CASE-0109 | Checked i side walk in and found T-stat on the wall was turned up. Adjusted T-stat temp down to 35°. | 14 | Thermostat Failure | FF12E266-8D8A-4C11-85FD-2566F8AA42D0
CASE-0132 | While checking all valves i commanded the solenoid on and off again and believe it was stuck and when it came back on the sub cool temperature was 54 deg and far from alarming the solenoid was potentially stuck during a call for sub cooler and had no temp diff across the in and out temp probes | 14 | Solenoid Failure | 37275F31-8E8C-453C-AAA2-181CE8306519
CASE-0106 | Found no case lighting operating upon arrival. Troubleshot the lighting circuit and found the ON/OFF switch had failed internally, preventing power from being supplied to the lighting circuit. | 14 | Switch Failure | D580842D-FFA9-4014-90E9-09FF6D949513
CASE-0214 | Found coil out sensor off by plus 3f. Put in a -3f offset. All parameters now match testo gauges. Found motor failed. Went to several supply house to match up motor. Motor has unusual bracket and mounting. Could not find motor. Picked up fan assy kit. Kit would not fit in place. Need to order motor from zero zone. | 14 | Fan Motor Failure | 62B3BDE2-DCF9-4C04-B1CA-E6BAD2FDA4BB
CASE-0423 | There is no water in drain pans..ice forming from both refrigeration and electric penetrations through ceilings of boxes…all penetrations need to be resealed. | 14 | Drain Blockage | 21012B0A-248A-4A5C-B8E3-20479C48BED8
CASE-0631 | Found case iced up. Checked and found plexiglass blocking return air. Case was recently cleaned and put back together wrong. | 13 | Drain Blockage | A9E09D4C-27B0-4E17-A350-85C47506A390
CASE-0360 | Found rack 1 not running because discharge pressure transducer was reading 350psi checked pressure and rack was actually at 75psi. | 13 | Sensor Failure | AFE1FF62-90DE-4348-B9A4-A7345C4DBC3D
CASE-0038 | Looks like for some reason the controller wasn't closing the relay for the TXV. | 13 | Control Board Failure | 8F377D5E-8E9A-4277-A2F3-018602303290
CASE-0583 | Found second compressor not running , traced wire back to a surge relay . Found terminal not on all the way . Put terminal onto relay and compressor runs . Relay internally starting to fail. Will need a new surge relay and relay board . | 13 | Surge Relay Failure | AAAC12B1-0939-46DE-B11A-2266B73C1D09
CASE-0220 | The unit was off by alarm with a low suction pressure alarm as a trigger | 12 | Low Suction Pressure | 5ABD8D54-3D9B-43C0-9F70-A44C846B4D2D
CASE-0239 | Disassembled case to find lighting socket to be shorted and sparking. | 12 | Electrical Wiring | 56DEEBE8-D7A9-47C7-9F3E-95648F78B339
CASE-0102 | Checked liquid line drier and found 5psi drop across. | 12 | Coil Failure | 02954A98-A6FB-4A23-A0A1-95916F3B0AB4
CASE-0157 | Sensor is faulty and needing too be replaced. | 12 | Sensor Failure | F8CB5451-BCDB-4276-8090-45EB74F32580
CASE-0065 | Found multiple alarms for DAFN and Proof/Rack Phase fail. | 11 | Control Board Failure | BB6C13D0-101E-4BA1-852B-A24D2B5646F6
CASE-0029 | Saw that RTU G had alarmed (a,b,c,d,e,f) but on arrival everything was down to temp . | 11 | No Technical Fault | B801B9EC-A512-40CA-BAED-42CDE71D19A1
CASE-0174 | High temp deli china walk in. Door wide open. Closed door watched cooler drop back to temp. | 11 | Drain Blockage | 27288A9A-D23F-459B-88B2-71275E539767
CASE-0236 | Water Leak coming from crack in pipe, and flowing down insulation | 11 | Pipe Failure | A2C0C548-B183-486E-A3DF-A750BE4E31AB
CASE-0772 | Found fan blades hitting on deck pans. Issue caused by fan shrouds not being pushed all the way down. | 11 | Fan Motor Failure | F7910351-B76A-4366-AF18-04B18C3E1C28
CASE-0588 | Check case found at temperature. No issue at this time. | 11 | No Technical Fault | 5E923F7E-9BA7-4012-964D-A0A99898E2ED
CASE-0427 | I found the case Joint between the service fish and service meat case leaking. | 11 | Drain Blockage | A4F4CF23-9046-4DC9-9B68-BE6796AA6C65
CASE-0049 | I opened the equipment and checked each component and it looks like new, I put it to work and noticed that the pan heater had products on top and these were burning, I cleaned and tested the heater and it works well, I left it working and waited a while checking its behavior. | 10 | No Technical Fault | E5E8D171-C9EA-4987-9AC2-DB74FF13FC9D
CASE-0725 | Leak checked rack made repairs to compressor #3 and b6 Epr . | 10 | Refrigerant Leak | A88796F7-6131-4B72-BD76-B803ADADA2A0
CASE-0816 | Replaced the main liquid line driers. No leaks found, no gas added. Performed a health check. | 10 | Drier Failure | F33BBDDE-C1C9-4CD6-A409-CC45EB27D66E
CASE-0292 | Found last alarm for low liquid was previous day at around 1400 Found previously the vfd was having an over torque alarm that isn’t present After previous repair and gas being added there is Currently no issues with full column of liquid at sight glass and no issues with cases Cases c12 had high temp event starting 5/26-27 and persisting til previous repair GC of remodel confirmed that no gas was added to the critically charged enviroguard rack C by remodel company after they added cases to the salesfloor Found subcool evg is ranging from -1.5° to 6.5° and not staying in alarm Verified transducer is accurate within 2psi and dropleg sensor is accurate within 2° Poor insulation on sensor so wrapped with layers of foam insulation tape Condenser not clogged and airflow is coming straight up from the condenser Found vfd intermittently alarmed but was alarming for inverter overload Inverter will have to be ordered as it was not overloading and amp draw stayed below 29amps consistently which is under the overload amps vfd is warm-hot to touch Vfds overheating has been an issue for a long time especially in warm months due to rack room being very hot Doors to vfd panels have to stay open for as much airflow as possible There is an evap for the rack room but it cannot cool the rack room sufficiently and is outside the design specs for ambient temp when the rack room is hotter There is not a data tag only asset tag for this evap Seems best option as this has been a chronic issue is to quote for condenser vfds to be moved to interior of store | 10 | VFD Failure | 4B279F2F-06A4-4B65-BDC1-50820841EE9E
CASE-0281 | Found weak airflow out of end of cases A02a and A02b. | 10 | Airflow Blockage | A3A04450-F4CE-4F47-969F-420A681C761F
CASE-0845 | Found steady drip coming from underneath case. After further investigation found water leak is coming from line set penetration. | 10 | Line Set Leak | 3FF5ACC0-C382-42D1-A3B4-3AE333FC2571
CASE-0258 | Compressor #1 is bad and needs to be replaced. It also needs a contactor 120v coil 30amp | 10 | Compressor Failure | BFBE8B43-7395-4FA8-BF39-3BD89008E6D0
CASE-0133 | Checked Ranco ETC controller and found the settings were unusual. Temp setpoint was 220 degrees, 30 degree differential and mode H1 (heating). Matched case A18-2 settings on this controller (27,2,C1). Case doesn’t have electric heaters or hot gas defrost. | 10 | Control Board Failure | F3DF72AE-B542-431F-8BA4-8ED9481A25C7
CASE-0311 | No active alarms in over 3 days . | 9 | No Technical Fault | 1FE9F707-F0D8-48C8-BBDF-615E6D235FF5
CASE-0734 | Found both controls in alarm for comm loss. Re scanned controllers and checked all equipment. Had to unplug 3 &4 main power modules and re scan to get out of alarm. | 9 | Control Board Failure | 5B7F8A1F-F167-4187-965E-9E050D02FA5E
CASE-0815 | Demand cooling solenoid was receiving power but not energizing. | 9 | Solenoid Failure | 9905A849-4AD2-4BB9-8694-45BFFA8BBE52
CASE-0328 | I found that someone set the setpoint at 3.2 degrees and the compressor wouldn’t shut off. | 9 | Control Board Failure | F5916B51-85FE-438C-9582-2422D42E1DFA
CASE-0527 | Case A8 missing temp sensor Run COM wire from board at rack. | 9 | Sensor Failure | C54FD8F3-B4C5-4FFB-A4F1-F8F6B2D86666
CASE-0575 | Only issue found was AC4 not communicating with the BS controller. Unit is currently operating in standalone mode and cooling properly. No further issues found at this time. | 9 | Control Board Failure | 21AE465C-6AF0-433F-95AC-919FE7E4993F
CASE-0403 | Compressor locked up. | 9 | Compressor Failure | 3D9189D0-A1AA-4324-8F3C-1FF5EB522743
CASE-0099 | I then noticed the damper was closed 25% not letting enough fresh air in to warm up the mixed air to keep the compressors going. | 9 | Damper Failure | 904C41D4-0477-4A9B-88DE-D3998982BA96
CASE-0617 | Found that the sweep was damaged and missing part of it. | 9 | Sweep Failure | 818DB7AF-5466-4E26-B0F0-1BF4F2AE45D6
CASE-0124 | Found unit flat on gas. Trace gas with nitrogen to pinpoint leak. I’m getting hits all over the aluminum evap coil. Compromised. Condenser and evaportor coils corroded and compromised, AEX no longer adjusts. The actual housing/interior of the unit is rusting away. All due to age and negligence from employees. I’m going to condemn. | 9 | Compressor Failure | D1B64947-8A08-4054-8BE6-FFB9BD1E3C9B
CASE-0329 | 6/2 Brackets for raceway came loose causing raceway cover to become detached, exposing case wiring. | 8 | Electrical Wiring | B1C8B8F6-AD2E-4B9B-BE1E-60AA45823884
CASE-0111 | Checked and found it over temperature. Checked and adjusted the EPR down half a turn Which dropped the temperature into range. | 8 | Control Board Failure | 7DA457FF-DD42-45D7-BCBF-C8EBC6A6AC8E
CASE-0405 | Fan plug had blown out. Suspect female harness connector is shorted and causing repeated plug failures. | 8 | Electrical Wiring | E3854B10-BB3C-451F-802D-4867B8C7969C
CASE-0375 | Found that bolts had fell off | 8 | Mechanical Failure | C47008B1-49AD-4760-8201-191D9D62F846
CASE-0233 | Doors are not sealing properly allowing air intrusion. | 8 | Door Seal Failure | 6CE07685-637C-4802-A8AE-349DDDF784C7
CASE-0502 | Condensation coming out from under reach in cooler on the floor. Checked into service channel and with manger. Went on top of cooler and found the roof sweating on top of the cooler. The sweating is between the spray foam and the top of the cooler panel. When feeling the top of the cooler panel can feel the cool air. Put a fan in opening to get air movement up there. Will turn in a quote to make repairs. | 8 | Condensation Issue | 67B625DF-7F9A-4959-A346-687056960DFC
CASE-0348 | Found anti-sweat controller in kick rail failed | 8 | Controller Failure | 75A15FF0-FF3F-471D-9E19-0389B8DF3CDF
CASE-0351 | Found VFD has failed and is not supplying 24V for corresponding terminals, which is holding drive out on STO. | 8 | VFD Failure | B18E1E10-081F-4E3B-8600-510C8BC508DB
CASE-0589 | I see major build up across A14,A15,A16. A14&A15 have build up on top sections where discharge air honey combs are. A16 has major build up on back wall. Got ladder and removed top panel, and see ice build up through parts not sealed. | 8 | Refrigerant Leak | 4BE05D3C-E6A4-4BC5-8CFB-11BF36D424E1
CASE-0864 | Found bad connection causing temp reading to be off. | 7 | Electrical Wiring | C6569A7E-26F8-4D32-B4A5-6E0FE3007240
CASE-0479 | Rack 1 has been down since 1am due to a power failure and never recovered. Found that the time delays for the cases were not set properly causing too much load on the rack when it came back on after a power failure. Rack is running and coordinators are aware of the issues. | 7 | Control Board Failure | E01CADD8-0C2E-4524-B561-7A21BEF7EE09
CASE-0134 | Went to the unit and cut the power off and swapped L1 & L2. They are now rotating correctly. | 7 | Fan Motor Failure | D4827B22-B88D-451A-B41C-AF2C42F96E34
CASE-0135 | A nut was missing from the bottom of the wall, and the one on the left side was loose; I installed a new nut and properly tightened the other one. Afterward, I cleaned the area of ??the floor where water had dripped and checked for further leaks; there are no longer any water leaks. | 7 | Drain Blockage | 25BBE5EA-04DD-4C4A-828D-5398F9E3717D
CASE-0316 | Upon arrival, I checked in with the manager and identified a water leak originating from the meat prep evaporator. | 7 | Drain Blockage | CADCB793-E212-4382-8F27-D142E0AC2BFC
CASE-0449 | Upon arrival I found the unit off. Checked gridpoint monitor and found the room was at setpoint. Checked all supply air vents and room temp and confirmed room was in temp. Spoke to manager about findings and he pulled up the temp log. Confirmed the unit was off as it should be. Unit would reach 74.5-75 degrees around 12:30 then unit kicks on. | 7 | No Technical Fault | E46A47D9-3284-4916-9DDB-E66F7549869C
CASE-0982 | Tech found leaking flare on condenser pump out line in machine room. Repaired leak. Added in all gas. All case temps and discharge temps came down. No alarms | 7 | Refrigerant Leak | 21085A93-3AC9-4B09-BC34-E5045C47CEF9
CASE-0804 | I found the mechanic thermostat was sticking closed | 7 | Thermostat Failure | FEC7FAA6-402A-4637-A195-A9A9075D1C27
CASE-0333 | Found pressure control differential set at 5lbs which is too low. Increased cut in to 35psi and set differential to 20psi. | 7 | Pressure Control Failure | DA21999D-964B-44D3-A701-7A0B83982FBC
CASE-0380 | Isolated and pulled old suction dryers and replaced with new. | 7 | Suction Dryer Failure | 98D20107-C5C2-4C65-A50E-4CBF1EE71657
CASE-0385 | Found that leak was coming from plumbing line. | 7 | Drain Blockage | 2BCE4283-FB7D-47A2-957E-D76030F3F8C1
CASE-0337 | Found two butt connectors that were the root cause. | 7 | Electrical Wiring | D2B12B4F-EE03-4FC5-92A8-8EFF5E68034E
CASE-0412 | B12 never alarmed today and the only case that even briefly alarmed today is B18c and that case has parts on order / known issue. Checked rack d panel and no alarms there. Went and checked B12, case has airflow and is at -11°. There is no active issues here at this time. | 6 | No Technical Fault | CF41CB7D-0721-410C-97EA-53D1DE71A251
CASE-0582 | Walked in found all lights and fans off. Walked around unit and found cleaning switch in off position. Turned back on and watched cases come out of alarm. Button and guard both hanging off and out of place. Probably hit by a rolling cart. | 6 | Control Board Failure | 310AFEF2-BD63-4719-8473-7C71C7965492
CASE-0747 | Found water was leaking out of the hot water pipes. | 6 | Pipe Failure | 7CC1B26C-B53B-4A75-8A04-96C19CB452C6
CASE-0574 | Found no incoming voltage supplying the case. | 6 | Electrical Wiring | DDFCC9A2-D60D-43DE-8545-5CA965ACA3CE
CASE-0317 | Unit is beyond end of life and needs replaced. | 6 | No Technical Fault | 3C4BF28F-C993-4A47-B537-7E196E551E5C
CASE-0549 | Found a new alarm for COMP A3 Alarm: Command Out State Switched ON alarm and COMP A2 Alarm: Command Out State Switched ON alarm. | 6 | Control Board Failure | F778DD65-0CA7-40C8-B84E-06FCDD7741C9
CASE-0823 | RACK D found relieve valve blew. Calibrate, no leak detected. 270# R-143a refrigerant added. | 6 | Refrigerant Leak | 80DAE092-0D7A-4748-BB0F-2135466D5CB4
CASE-0543 | Found defective LED driver. | 6 | LED Driver Failure | E885BE94-DD5B-4D75-99D5-3B36F8DBA1C7
CASE-0501 | Evaporator fans working, no ice on coil. | 6 | Coil Failure | 51230F01-4674-4B50-B970-D13A3D60BC64
CASE-0634 | Unit alarming for fan proof. Found unit turned off at breaker and disconnect. False alarm | 6 | No Technical Fault | B70E2A09-3F96-4FA6-B18D-B133A9364B2D
CASE-0972 | Upon inspection, found the case end panel separating from the body of the case. Ice formation behind the panel has expanded enough to push the side panel outward, pulling the mounting screws out of the panel. | 6 | Panel Failure | 460C35FF-3889-4987-82F8-B3A5A1A19699
CASE-0609 | I observed signs of moisture and active water dripping directly onto the unit from the roof above. | 6 | Roof Leak | DA83269F-CDFB-45EA-AD87-F32C9A5A66C5
CASE-0324 | Replacement of two failed water Therma-Stor tanks in mezzanine level mechanical room | 6 | Tank Failure | 9B1CDFB2-51BA-4F01-BD6D-12FC6ED08709
CASE-0374 | Found LL strainers in a12 a13 and a14 dirty. Removed and cleaned. | 6 | Drain Blockage | 38DB04E9-BF56-4628-8BD4-DC318F3D5155
CASE-0435 | The breaker for C7a is sticking and needs replaced. | 6 | Breaker Failure | 803900FD-1B66-4C9D-9CAE-CDA8CA7E65D5
CASE-0012 | Found WIC F01 also running warm | 6 | Compressor Failure | 76A8E494-4147-4182-A17A-77F47E63B629
CASE-0176 | Found stage 2 compressor with a bad high pressure switch, bypassed switch and checked operation all 3 stages running at this time. Will need to create quote to install 1/4” swivel tee and new pressure switch. | 6 | Contactor Failure | 45CB4045-1061-4ACD-A495-14D8BA6C69BB
CASE-0060 | Found one of the pump motors for the syrup regulators was not being able to pump at the psi needed and was releasing the excess CO2 to compensate. This was causing the CO2 alarm to go off. | 6 | Pump Failure | F99EA436-E925-4CB0-8AFC-34072CD4B445
CASE-0206 | Found nut where solenoid sits on very loose. Tighten down connection. Leak repaired. | 6 | Refrigerant Leak | 1935F1AE-A9A6-4CBE-A32C-ACA31B0364C2
CASE-0028 | Found NEW mister system cannot keep condensors cool and compressors online !..had to hook up the old sprinklers and even a lawn sprinkler to keep it all online…condensors here are falling apart…noted wires cut to some of our old sprinklers ? | 5 | Condenser Failure | 2110BA10-B640-43D5-9092-AF680698CEA2
CASE-0313 | This RTU is not programmed correctly. | 5 | Control Board Failure | DFD597E0-702F-4376-945B-DF3928CB88D2
CASE-0226 | Found idcm module has failed. | 5 | Control Board Failure | CD19552F-6BE3-4B20-A19C-079264509791
CASE-0366 | Removed cord from actuator and found water intrusion has caused the actuator and cord to fail. Found water was not running on gas chiller despite 45% RH and temperature on roof being 99.3°F. Guntner displayed 100% RH (handheld sensor read 45%) meaning it was not trying to run humidification. Unwired AI-2 due to failed RH sensor. This allowed the Guntner to go into humidification mode. Despite calling for water the Belimo valve did not open. Confirmed board was send 24v power and approximate dc signal to Belimo valve. Removed Belimo actuator and manually opened water valve. | 5 | Actuator Failure | 2FC5ED45-A901-4479-A6E2-BB1AC265D1DC
CASE-0186 | Located shorted ballast also one door not closing | 5 | Electrical Wiring | 6807962C-E069-487E-95C8-D53D87974DBD
CASE-0117 | Coils had some dirt build up. | 5 | Coil Failure | E5B41615-5ECE-415B-8971-9D9C823AA427
CASE-0429 | The issue was someone had to turn the fans off at the switch and forgot to turn fans back on causing beer cooler to high temp. | 5 | Fan Motor Failure | 6E92A009-B3DF-4656-9BA3-C5CAE8E4C343
CASE-0694 | Confirmed EPR stem is backed out all the way on epr so system runs on rack pressure. | 5 | EPR Valve Failure | 02FAC9CB-55F5-4FC1-A59A-B9C4D49929FC
CASE-0390 | Found the pulley is unusable | 5 | Pulley Failure | 32B0B6D4-38D5-4DC8-9D79-48D64FE00A1E
CASE-0368 | Traced water leak to the ice chute gasket leaking. It leaks water down onto the agitation motor body, then into the insulation for the drain hose, eventually making its way onto the counter. | 5 | Gasket Failure | 0C55ADEA-982F-4634-8BC4-D09E98D6D527
CASE-0249 | Removed the plunger from the door. Cleaned off the plunger. Added new grease to the plunger. Put the plunger back on and door is working properly. | 5 | No Technical Fault | 0AC0B684-C9AA-4A8B-93C6-9E74EB638696
CASE-0952 | Replaced TXV in sys C01. Not leaking, mechanical failure. | 5 | TXV Failure | 70369624-6D10-4635-8C14-2EA66C251010
CASE-0493 | Inspected ice machine, found dip switch set to off setting, switched to ice setting, no change. Waited out a possible time delay period, no change, relay for refrigeration not making the switch, issue is isolated to the board, will require a new control board. | 5 | Control Board Failure | 3B9BEFD9-AF28-4B8A-A05A-716135AC65D2
CASE-0760 | I found the spw5 expansion valve making the noise. I held it down and adjusted the position of it and tied with some zip ties to hold it in place. Once I did that I saw the temp began to drop on the RDM and it came out of alarm. I went to take the coil off and I pushed it down slightly while trying to take the top clip off and I noticed that the valve opened properly and started feeding correctly. As soon as I let go the coil pushed up slightly and disengaged. Took coil off and verified that valve was working with a magnet. Noticed that underneath the coil it had a curved spring looking thing. This is what caused the coil to lift slightly and disengage the valve. Removed it and put the coil back on and the valve worked correctly. I don’t know why manufacture puts that piece there; this issue has happened before where that piece causes the coil to lift slightly and prevents the valve from opening. | 5 | TXV Failure | 6B601A3E-4337-4876-9A57-9290D528A3FA
CASE-0492 | Inside release damaged by impacts. | 5 | Component Damage | FEB7137A-9AF1-4671-A487-8AE085BAACF6
CASE-0461 | Found no refrigerant flow. Gauge reading approximately 180 on suction. Override the EPR from 50% to 100% caused no change. Found 180 PSI on the circuit side of the CDS valve and 46 PSI rack suction, indicating a restricted CDS valve. | 5 | CDS Valve Failure | 5570F667-697E-4A3E-9ED6-20D19BDEAD95
CASE-0161 | FOUND LEAKING PIN AND CAP ON EVAPORATOR IN F1 | 5 | Refrigerant Leak | 7B7444D1-9225-41F9-9729-57A2C0A1D3C5
CASE-0756 | Found compressor began to trip on low pressure due to unit being in defrost | 5 | Compressor Failure | 27B12B8E-5743-403B-AF47-C9DF503341D9
CASE-0340 | Arrived on site and checked in. Verified door operation and door open sensor. Both functioning properly. Checked out with manager Trevor. Job complete | 5 | No Technical Fault | E20DC233-F80A-47CB-9698-20C72A993F34
CASE-0334 | I noticed while monitoring case, when a customer opens up a door and closes it, another case door opens on its own. | 5 | Door Mechanism Failure | 6DB04355-7165-4AD4-B52C-DADFFF45A8C3
CASE-0607 | Found actuator with power but noticed motor broken. Which is the housing is cracked and not making full contact on shaft for the 3 way valve. | 5 | Actuator Failure | 2943F2B3-2933-47AE-9C2A-B3718E7AFD4F
CASE-0480 | Rack A is back in communication. | 4 | No Technical Fault | EE625428-4B33-4F3A-8752-4839EF72DDDF
CASE-0372 | When I arrived, I found there was no leak present spoke to the manager, and they informed me that the leak has already been repaired by a roofer. | 4 | No Technical Fault | 24B4E3CE-D76C-466E-B074-BF8FFBBA9924
CASE-0666 | A19 failed and bypass to test cooling and cooling kicked on. Removed failed A19 from AC unit and installed thermostat, all stages of cooling are now working and pushing 46° supply air. | 4 | Control Board Failure | 0AE67C03-E0AF-4B95-ADE1-45BE38EA0C67
CASE-0361 | Found supply fan VFD was tripped on dc bus over voltage. After calling Yaskawa And adjusting VFD multiple times. Supply fan motor would over amp and trip VFD. Bypassed VFD. Found one leg of power would get up to 11 amps and drop back down. VFD max amp setting was 11.6 amps. Motor is rated for 9.1 amps. Unbypassed VFD. Lowered VFD to 50 hz. VFD now only pulls around 8 amps. VFD is not tripping. | 4 | Fan Motor Failure | 39DF6A57-CF2E-48A0-8A65-91F8D0DE93CE
CASE-0112 | Chiller #2 off on water latching fault due to programming issue with pumps shutting off same time compressors do. | 4 | Control Board Failure | 23898087-0EB4-43DC-999B-91ED732FE3D8
CASE-0706 | Coil appeared clean, but inside was plugged up. | 4 | Coil Failure | DDA3C5A8-7DBD-4CF4-8B9E-F84ECDE0A7A7
CASE-0121 | The outer pane of glass was broken | 4 | Glass Door Failure | 5D7644B1-FB33-49B5-9C1C-31609E90BBD8
CASE-0530 | Shaft seal is leaking oil. LT-2 compressor. | 4 | Refrigerant Leak | 9B7E88E9-7FA8-4A9B-A027-57FCF86AE644
CASE-0378 | Battery is an odd size tracked down batteries locally picked up new batteries returned to site and installed alarm cleared | 4 | Battery Failure | F35F4398-634A-4117-93EA-5555CC4CBD88
CASE-0438 | Confirmed Leak detector override for 8 hours. | 4 | No Technical Fault | 3C03CA0A-8066-4348-B192-DEA991AC1F34
CASE-0482 | Found compressor unplugged from output, and blew out drain. Case took long time to pull down due to possible leak. | 4 | Compressor Failure | FC2EE93A-75C6-496E-95D5-BB6B4CB0FCDC
CASE-0477 | Vibration appears to be caused by structural resonance of the compressor mounting support rather than an internal compressor mechanical failure. Recommend quoting a welder to inspect, reinforce, and reweld the affected brace and associated mounting structure as needed. Compressor should be retested after repairs are completed. | 4 | Structural Resonance | D9117F3A-BF39-4305-B844-D36080FAAEC6
CASE-0920 | I checked all fans motors none of them were making the noise.I checked and tightened some loose screws, evaporator noise is reduced. | 4 | Fan Motor Failure | F6C4F2D5-43D1-4EF7-8706-B874A84EB363
CASE-0499 | Found several doors sweating. | 4 | Drain Blockage | 8AE93340-C4F5-4027-99C2-89164BCA1731
CASE-0148 | Found asset to match Case ID RBPR09B. Case is high temping. Case has good airflow but is having a hard time cooling. Noticed this case is missing one honeycomb vent. | 4 | Coil Failure | 349EC4B5-8528-4403-841B-9C2E3B81AB5A
CASE-0440 | I continued removing the ice with hot water and found an electrical short circuit originating from the rear panel of the case. | 4 | Electrical Wiring | DD3D48F2-F0B8-40AA-B62B-8D300739FE1C
CASE-0172 | Found a factory jumper not working on right side . Took it out tested it moved it over and now it’s all working back at temperature | 4 | Control Board Failure | 6FF978E4-4898-496F-AAE4-A4D6813FDC6D
CASE-0125 | The hot end on the surplus ISLA has a couple of shelves not working. | 4 | Shelf Failure | 5F605880-280A-4957-B3B4-00B4EA3C0D28
CASE-0766 | fixed leak on comp #2 rotation switch | 4 | Refrigerant Leak | 678C2B19-B322-488D-891C-0D85CF4F455F
CASE-0774 | The Electronic Expansion Valves (EEVs) were not communicating correctly; they remained closed. | 4 | EEV Failure | FAFA4741-EBCA-45C5-A44F-34434DCD67B4
CASE-0525 | Reheat Alarm on FLO HVAC unit, reset the unit and the alarm went away couldn’t get it to come back on follow up needed. | 4 | Control Board Failure | EB5A2C6D-55B0-4F98-AD55-9B5AB6F8FA73
CASE-0902 | Found a fan cover off on evap B. | 4 | Fan Motor Failure | B8508BD7-2DEE-4AA0-AE76-7378D49D1300
CASE-0393 | Found RTU1 has 2 stages of cooling but is only configured for 1, verified with Gridpoint tech support. | 4 | Control Configuration | 1E6FEC12-B219-44A4-A44A-9DFBECB5B58F
CASE-0723 | Found that the bottom of the fan plenum does not sit flush with the pan. I made 2 shims and put them under the plenum to stop the vibration. | 4 | Fan Motor Failure | ED10D845-288C-4B26-8B15-76C6F6687D6F
CASE-0223 | Found operational with error code evap temp diff. Accessed return and supply, found air filter to be plugged. Removed filters, allowed unit to run. Found no longer alarming for evap temp diff. | 4 | Drain Blockage | C865B786-AB33-4248-BFFB-EAA4C19F6892
CASE-0265 | Arrived and found unit idle | 4 | No Technical Fault | B7ECBB1B-B2E7-4D43-8F15-A46DDFA2BB7C
CASE-0295 | Used multimeter and determined that Danfoss temperature control with sensing bulb was not working | 4 | Sensor Failure | F9195CB7-2679-4DC0-95E1-FF8C38AEDD2A
CASE-0269 | I checked the thermostats and found one set to heat and the other one was off. I moved them both to A/C and set them to 72 degrees. | 4 | Control Board Failure | 8A8C11E0-AB1E-45B1-A709-945B59B500A7
CASE-0841 | Found the GFCI tripped. Reset it. The machine started up but as soon as it tried to defrost, the GFCI would trip again. I ran an extension cord and got the ice bin operating. Monitored operations. Traveled to supply store and purchased new 20 amp GFCI outlet. Returned to the store, turned the breaker off, changed outlets, turned the breaker back on. Then plugged the ice bin back in and monitored operations through defrost the new GFCI tripped. I looked through the wiring and found 1 possible connection loose, I tightened the connectors for a better connection. Started the unit back up and the GFCI tripped again. Contacted tech support had to wait for over an hour and a half for a response. They informed me to replace the receptacle again. I traveled out got another outlet and installed upon returning to the store. The unit is now operating properly and has tripped in over an hour, I have forced defrost several times. | 4 | GFCI Failure | E483B0E9-D097-41EE-A36A-6A61D098E65F
CASE-0675 | Poured water down the drain to make sure the units were draining. The drains are working ok at this time. | 4 | Drain Blockage | 826967E5-1955-4DE9-B304-A1F48EF30BC1
CASE-0610 | Found “cloud” forming in corner of machine room. Located blower on cracked seperator body. Welded over large leak/cracked oil separator. | 4 | Oil Separator Failure | 6A61AF2A-E502-4FA8-B499-58983669793D
CASE-0687 | Arrived and found inducer motor to oven was making loud noise. | 4 | Fan Motor Failure | B4534BF3-5B71-4DA9-9458-A27700A4E51C
CASE-0131 | This unit is GFI protected at wall socket and was tripped. Pulled unit out away from wall to gain access. Reset GFI and unit came back on. | 3 | GFI Trip | 1E0D23F5-14EF-4F4D-94BC-1B015E373967
CASE-0545 | Ak2 panel alarm. Check through all Danfoss panel no active alarm present at time. | 3 | Control Board Failure | 2B6EE466-50FB-4CFA-B10D-09213CDB7CF6
CASE-0546 | Picked up motor from supplier. Travel to the site install motor on freezer one right side from front and tested operation freezer one is back on now . | 3 | Fan Motor Failure | D794973F-0E5D-4DBB-8EE0-759505ACA10F
CASE-0793 | found leak coming from hvac duct above WIC, during hvac pm I noticed heavy condensation on supply duct that’s uninsulated | 3 | Condensation Leak | 42FB7E9B-195F-4694-B176-F49094B6EA0E
CASE-0645 | Case is rusting out badly. Evaporator coil looks to be bowing in causing center to sit lower than the ends. Highly recommend changing out cases. Cases back down to 28 degrees and within 2 degrees of each other. Cases back down to 28 degrees and within 2 degrees of each other. billable, cases beyond repair | 3 | Case Failure | EC877761-ED87-4E76-A401-30119B5C4F41
CASE-0394 | Found system satisfies and reaches 36 before cycling refrigeration on. Made slight adjustment to EPR and monitored. All sections now at 31-33 degrees F. | 3 | TXV Failure | C927B458-4107-4C65-B5C1-0B3ED1918C3D
CASE-0244 | I check for a water leak in the deli department, review the level of the tray, and it is uneven. I correct the level of the tray and adjust the insulation in the department. I check the low line, monitor for leaks for a while to see if it happens again, and stop the dripping from the tray. | 3 | Drain Blockage | C85098C6-FB80-481D-A838-9D7EEBD173A4
CASE-0970 | No notes were left for what cooler was temping high. Went through sales floor and did not find any temperature issues. | 3 | No Technical Fault | DF7EBE2A-D69B-45AD-BF0D-8B10687751B6
CASE-0092 | Case at temp, out of temp during defrost. Mullers hvac unit economizer fully open. | 3 | Economizer Failure | 67B6418A-1B11-4B9E-AA91-584D2F0B748E
CASE-0388 | Found the oil line rubbed out between the reservoir and the oil filter. | 3 | Refrigerant Leak | ED5B4626-26E5-4812-82A7-5ACBED7F1037
CASE-0551 | Diagnosed cause of flow issue | 3 | Flow Fault | 3E02D059-7D86-4E6D-A8F6-4D94047FA223
CASE-0202 | Found the c-19 line up avg 38 deg. Check epr found at 30deg due to comp C1 had just shut off approx 15 min before my arrival traced problem to line side connector at comp , repaired connector , had issues maintaining suction set point due noticed controller reset itself while on site , monitored operation until stabilized , adjusted epr to 24 deg cases now avg 34deg | 3 | Control Board Failure | A49027B7-A0F0-48B9-8DCA-5810844445B6
CASE-0441 | Cause of high temp alarm is proximity to exterior doors and customer foot traffic increasing load on case | 3 | Load Increase | 985C9FD1-9B18-4C6C-8E74-FD238B6ABABF
CASE-0277 | Found small piece of insulation torn out due to past water leak and now forming condensation, this is supply ductwork, customer provided wrap insulation. Cut out damage insulation and reisulate it to stop condensation to form in supply duct and start leaking. | 3 | Drain Blockage | E42EAF05-EC52-441F-95BE-1811E970623C
CASE-0192 | Inspected the unit and found that the lid for the bin doesn’t securely stay on anymore allowing warm air to enter the bin and melt some ice. The auger motor for the ice is worn due to lack of maintenance and occasionally scraps the lid causing it to come loose. | 3 | Auger Motor Failure | E05F0F2B-FC21-448A-A0AA-D8192D67EA7F
CASE-0765 | The cap tube is plugged. | 3 | Cap Tube Failure | 5B9F01D5-84F1-4A83-A3BB-04BEB9468358
CASE-0786 | I arrived at the store and consulted with the manager. I then proceeded to identify the equipment, which was operating but had a damaged power cord that could have caused an electrical problem or an accident. This cord was damaged when the equipment was moved for cleaning. The cord was repaired and the equipment was restarted. The temperature was not affected. | 3 | Electrical Wiring | 7AEF20F8-B8D6-4F8A-AC03-5E180B1771F4
CASE-0242 | Remove 4 failed and undersized air curtains | 3 | Air Curtain Failure | AE14F211-16EB-48BE-B8A9-FECCFD9BDEE7
CASE-0146 | Checked refrig rack and controller. No issues found. | 3 | No Technical Fault | B4C0183E-ABD8-4A99-9F5A-93591383967E
CASE-0428 | The gas valve was closed in the control and the gas lines was insulated by other tech. | 3 | Gas Valve Failure | CA52414A-7585-477B-ABA7-6AFBB44A0F18
CASE-0044 | Alarm Message: MULTI CASE TEMP | 3 | Sensor Failure | BF737173-8FF6-4780-A579-1E6558D71A97
CASE-0911 | The transducer is changed, but the heater cables were burned and damaged the connectors of the suction sensors, return, and transducer cables. I found shopping carts, removed all the shelving, disconnected the fans, closed the refrigeration unit, turned it off, removed the fans, moved the coil slightly forward, and replaced the rear heater. I placed the coil in its position. The front heater was a little smaller, so I spoke with the manager and went to the office to find the correct one. I returned and installed it. I placed the fans in their positions, made all the electrical connections, closed the unit, turned it on, connected the fans (they were working correctly), replaced all the shelving, opened the refrigeration unit, and as the temperature dropped, I cleaned the area. Once the temperature reached acceptable levels, I placed the unit back in its place. Manually defrosted the unit to verify the heaters were working correctly. Once defrosting was complete, the unit entered cooling mode, lowering the temperature to within parameters. I left the call open because it needs parts that are already ordered. Done, report to the manager. | 3 | Electrical Wiring | DBBDB5CB-7462-448C-9218-159159A66F23
CASE-0513 | Arrived on site and checked in with mod to change case from fresh to frozen. Located case and made change on controller. Monitored system to make sure it made temp. This call is complete. | 3 | No Technical Fault | E035EC70-909A-48A1-94D2-C5753D70E886
CASE-0521 | Tech found bypassing yesterday on another call. Pumped down and isolated circuit, opened valve and rebuilt internals. Valve no longer bypassing in refrigeration mode | 3 | Valve Failure | A23D7600-F1E1-40A8-989A-50ACA774C818
CASE-0838 | The compressor and condensing fan was running. My evap fan was running as well. Coils were clean too and suction line is cold. | 3 | No Technical Fault | 4A484A96-0739-4049-9B77-4727B8885887
CASE-0776 | Modulating valve was not getting proper signal. Signal goes from controller to signal board with a 0-10vdc signal. Then to a signal conditioner board, before going to maxitrol modulating valve. Was not getting 24v to that board. Went through control wiring, fault relay that breaks 24v common was operating properly. Eventually found bad wiring connection that prevented 24v from getting to signal conditioner board. Repaired wiring. Unit now runs heat as it should and modulating valve is opening to allow proper gas pressure at the burner manifold. | 3 | Control Board Failure | 75D300C5-5570-4F63-910E-E0471682CC21
CASE-0043 | Found 2 controllers M5 and AC controller with wrong dates and times. | 3 | Control Board Failure | BC6CCD90-EA06-40C1-BCAB-7F8A6F2495CD
CASE-0904 | Found freezer 4 suction king valve stem cover is rusted closed and will require replacement. Found freezer 3 discharge king valve is stripped and stuck, unable to drive stem in to take pressures, this will require replacement. | 3 | Valve Failure | A9E5DE17-3979-43F0-BB51-57D8A0D60308
CASE-0528 | Pump down all 3 racks. Bring tower offline. Remove and replace both pillow block bearing and lubricate thereafter. Bring tower and racks back online. Remain on site to verify operations after repairs. | 3 | Pillow Block Bearing Failure | 83533348-4A1E-40B7-A5EC-E639CB934BCA
CASE-0512 | After connect to the leak detector found it it stock on reading. Verefied that by leak check in compressor rack and nothing detect. Soon I open the leak detector it went to 1.75ppm and it seems that something was trapped inside the leak detector. | 3 | Sensor Failure | 7F179C38-B70E-4EC9-97AC-78C23EB4097C
CASE-0965 | Found water draining from the cap at the basin of ice bin. Previous bin had no drain attachments, and likely where leak was from. | 3 | Drain Blockage | 1F505B5A-5289-41A3-A823-1C01501E54A5
CASE-0729 | We did check the case last Friday and we ordered the danfoss EEV valve for it. I found the EEV1 with a superheat of 36°F degrees set point (12°F), and EEV2 at 13°F. I reset the valve to allow it to reset. Once it was reset it pulled down to 13°F of superheat. | 3 | EEV Failure | D7E8D924-E75D-4DA1-8236-5013B3E6720A
CASE-0636 | Called digital assets and confirmed controllers were back online and they were, no further action needed. | 3 | No Technical Fault | DCEFA252-62F9-460C-96F0-9B9DD21DA7CD
CASE-0284 | Found that store charged case from low to medium temp with toggle switch causing the alarm. | 3 | Control Board Failure | 31D6C5B2-8BA1-4196-AA63-9F07BE89D2AB
CASE-0426 | Found open line in alarm panel causing auto shut down. | 3 | Control Board Failure | 0889A83E-1A2A-4FEA-B0DE-0C9BF72379CF
CASE-0498 | Most likely the bunker temp switch got hit and was switched back to medium temp. | 3 | Sensor Failure | 991DA37F-59EA-4894-B556-8E55A71AD1F1
CASE-0608 | Ahu 1 seasons, four found that both compressor crank case heaters not working and need to be replaced | 3 | Fan Motor Failure | BFB0C7F9-2923-49CF-BD73-39D6C5511E86
CASE-0880 | Compressor tripped | 3 | Compressor Failure | 7A61FBDD-8611-4A78-ABD9-DF39D09211D5
CASE-0213 | Tryed to use username and password to access controller unable to access controller. Reset all controllers and waited for controller reboot. tried yo enter username and passwords again access still denied. | 3 | Control Board Failure | BD5474C1-D3AD-4625-95F4-95B508BB7AA3
CASE-0705 | I found the EEV1 with a superheat of 36°F degrees set point ( 12°F), and EEV2 at 13°F. | 3 |  | 9774A7D7-F6E4-4D11-B3FA-4C3AB2D9C6CB
CASE-0594 | Located new ice machine in receiving area, removed old ice machine from Starbucks, installed bin and condenser, repiped copper drain line, verified drain working properly, wired up machine and started up, cleaned up mess, machine now making ice, checked ops. Completed | 3 | No Technical Fault | 444AA0B7-1164-4846-B527-AD6A4A6F1FF7
CASE-0673 | Found medium temp compressor 1 toggle switch was off because it must’ve been hit by a cart. Had trouble getting the compressor to operate as the switch was damaged. Finally got it to run and then checked other compressors. A couple of other switches were broken off and low temp compressor 2 switch was bad and compressor wouldn’t operate because the switch is bad internally. Ordered replacement switches and replaced all five switches. | 3 | Switch Failure | 7B000349-EE40-410B-A803-A0E5D232708F
CASE-0209 | After discussing the findings with the Walmart technician, we determined that the following components should be replaced: Accumulator, Suction service valve, Transducer, Discharge temperature sensor, Capacitor, Discharge pressure switch, Filter drier. | 3 | Component Failure | C612A773-BA58-44ED-8AB5-57C0510F2E8A
CASE-0318 | Found that there was water leaking from a hose on the roof. Shut off the water from the hose bib which stopped the water from leaking from the roof which causes the leak. | 3 | Drain Blockage | D1693A2D-3782-4D6D-AF8B-8947E8CF33C5
CASE-0919 | I had checked the E2 and found one overcurrent alarm on the system and the unit never went out of temp. | 3 | Control Board Failure | 0CD10EBC-F1BA-4B07-BD6A-87F4441DB075
CASE-0615 | Beer cooler drink / produce section is the case running to cold. | 3 | TXV Failure | 15D035B3-B053-41C5-A4B5-4E5B4CD2F8DC
CASE-0472 | Found all three windings open, suspecting internal overload was open due to overheating. | 3 | Compressor Failure | 48E2B70A-F04B-4544-BD26-4787EDF1F3C0
CASE-0160 | found both delta one case and delta two seafood case in defrost on arrival, removed both cases from defrost cycle and monitor temperatures checked all compressors are running. All condenser fan motors were running suction pressure and discharge pressure, called digital assets to verify case temperatures at setpoint and operating at this time. | 3 | No Technical Fault | 23E86797-9C6B-4A87-AED0-E1C07C08902F
CASE-0489 | Found the unit drain never installed. And the unit gas pressure is to high the gas pressure should be entering the unit about 7 to 14 water column but pressures over 35 WC, the unit need the gas pressure regulator wich should install during installation. Shut off gas line due to be summer and the store not using heat. Found some wiring burned out and create short. Due to vibration on the metal. Removed burnt wires and rewired the unit with new wire. Found the one the wire connector got loose and can out of terminal number tow. Repaired the connector and placed it on correct terminal, turned the unit on and made sure unit started working. | 3 | Gas Pressure Regulator Failure | FCFCB9D2-BF19-4EB7-B917-29F9283B4BDD
CASE-0671 | found no remote sensor installed for controller, going off Tstat temp and see a 3 degree difference, Tstat reading 73f, smart sense reading 76f, not near the data tower, no excessive heat load near sensor, recommend to have a remote sensor installed by gridpoint | 3 | Sensor Failure | 8C9EC635-9831-4238-8ACC-24841863A4D1
CASE-1000 | It was still attached, but it was just missing screws, so it was loose. | 3 | Electrical Wiring | EDD8A4A8-8094-4A64-92BB-879ACB3096C8
CASE-1057 | Went to controller to verify which evaporator was high temping. And found Evap 1 to show nearly 10° higher on all inputs. Went back to case and checked for restrictions across filter drier, found no TD across drier. Began pumping down case to perform EEV valve body check. This EEV is a semi hermetic valve that can open up to access a filter screen and to clean internal components if needed. Once case reached 0psi, I opened up the EEV body and found minimal contaminants. Cleaned out body and then fitted back together. Opened up system and began monitoring temperatures. When putting EEV coil back together also noticed that the threaded flange keeping electrical connections in place was worn out not allowing full connection. Fixed this by removing the flange from threads on screw. Pushed the flange into the coil and then plugged in connector. Screwed in the securing screw and fixed the loose connection issue. first call the vlave coil was bad this was another issue that was on the same valve not a call back. | 3 | EEV Failure | D8571C68-649C-40CA-AFF7-5BB3B9AA15F0
CASE-0986 | Found puddle of water across back room coming from back of ice machine. When looking under ice bin there was water splashed on the wall indicating the leak was coming from somewhere high. Scooped ice away from ice chute so machine would run a cycle. Observed back of machine and saw water dripping steadily from just to the right of the drain connection. Removed from cover of machine and discovered base frame of ice maker and top of ice bin are sagging approximately 1/2” in the center. This is tweaking the evaporator assembly away from the water tank and allowing water to leak along the rear of the machine during a freeze cycle. | 3 | Coil Failure | 1D4098A3-5FFB-4487-A431-14F3B2C46E27
CASE-0808 | Found compressor delay switch Zero’d out (no delay). | 3 | Compressor Failure | 11D67FBE-40CC-476B-87EA-4D85434331EA
CASE-0807 | Found unit extremely dirty, found leaking bottom auger seal and drain valve leaking by. Found float valve sticking occasionally, but system showed no alarms while onsite. Ran unit, verified appropriate supply water pressure and produced some ice, but production stopped after 15 minutes and refrigerant started flooding back to the compressor. Due to age of the unit and multiple failing components, recommend replacing ice machine for cost effectiveness. | 3 | Compressor Failure | A5EBD26E-E2F8-44BA-B6A8-9CC4ED81FDDD
CASE-0624 | Found drain receiver box over flowing, checked acorn system and found pressure was at 4.7 and not shutting off, went and checked around cases and found air not stopping behind ice cream case causing cheese case not to work properly, talked with Tim at P&P, had me check out a few things and told me to replace extraction valve, controller and check valve. Replaced parts and checked operation everything is draining and working properly at this time. | 3 | Valve Failure | 6684E795-F3E2-4F8E-878C-E50C838405CA
CASE-0670 | found conduit damaged to receptacle, found wires rubbed through inside the conduit, found water inside the conduit making contact with the wiring underground, found receptacle mounted to the unit with zip ties making contact with the floor, inspected receptacle and found water leaking out of the receptacle | 3 | Electrical Wiring | 805F10CA-E6B8-4C11-831A-EB84D0E00AF3
CASE-0565 | Bulb was in the wrong location causing case to run colder than necessary. | 3 | Sensor Failure | FB3BAD8A-DEA1-4D25-9528-50E2BB41C154
CASE-0002 | Received glycol supply pressure alarm. Bot supply and return pressure are trending steadily downwards. | 3 | Refrigerant Leak | 9F006DDE-8C7B-4FF7-A3E2-1F82F6370E51
CASE-0322 | Found comp 2 to be rattling and sounds like something is broke off internally. Has internal damage and will cause a bigger issue in the system and is tripping and alarming on the controller. | 3 | Compressor Failure | 474C8195-EB89-482D-B9FB-74AAD4BD3E64
CASE-0304 | Condenser B was found overflowing | 3 | Drain Blockage | 9F5761F6-3A64-4F1B-9F0B-98CCD34FC405
CASE-0628 | Found 4 of the 6 door closers on case not functional. | 3 | Fan Motor Failure | D1A660AE-0D44-43D9-A99B-CC8686E984A9
CASE-0469 | found rtu zone 2 running in high with 80% humidity. Found unit in heating no faults. Called Christian at r3 and he made minor parameter adjustments and is now in cooling mode, store humidity dropped down to 75%. | 3 | Control Board Failure | 25D9DE87-E186-4D83-A01C-5EBD1830B0AB
CASE-0668 | Tech found check valves not isolating the pump that needs to be. | 2 | Check Valve Failure | 043E34EC-D606-4BE3-A257-8875924026DD
CASE-0748 | Found surge tank and found no sight glass balls floating. Due to low liquid in the system I found that the temperature increase in the case was directly tied to the liquid level being low. | 2 | Refrigerant Leak | E96C8DDC-7A23-42C1-981D-7AF8CBC18394
CASE-0510 | Found unit becomes quiet once certain areas around supply and return are sealed. Proceeded to tighten some screws and place sheet metal tape around air gaps where sheet metal tape is missing. Unit became quiet. | 2 | Drain Blockage | 3FCA62EC-86EC-4AC4-8219-1E44E7F602EF
CASE-1048 | Found a piston was missing and destroyed. | 2 | Compressor Failure | 8AF5CB93-1B07-4DEC-9DA6-87BA874C3BE9
CASE-0657 | Found problem to be caused by sump pump bad in gas cooler . | 2 | Sump Pump Failure | 50D4E263-318D-4CF5-9310-6BEA2899EBA9
CASE-0993 | Found water leaking from top of box to the outside running down causing water on outside of box. While inspecting where water was coming from found a drain pipe above walk in box pouring water in from a 90 fitting. This issue is what caused all water on outside and inside of walk in box. Coil has 2 distributor tubes cut and capped due to leak in evap. | 2 | Drain Blockage | E4FDA0C1-B868-4C4A-8AAE-56B68F44E966
CASE-0676 | Found fan shroud was not sitting all the way down and was open in the bottom and flow air over coil. Ran hose high and on top of ladder as to not be on the ground. Deiced case, put back together properly, case pulled down to temp. While waiting on case to pull down I noticed sightglass was flashing, and started leak checking, found no leaks but did notice that the Evap in Grocery Freezer was still valved off and on in the I/C freezer that shared with Grocery Freezer was cut out. Added 50lbs sourced from onsite. Tank - 51021LL-R404A-04072026 Filled site glass. We quoted to replace Evap in August. case is operating per design and 9 amp on both defrost heaters. This call is complete. | 2 | Valve Failure | 3DC6CAE4-3D7A-4FFC-BB1F-4D9AC395F47A
CASE-0738 | I found that the keeper pin that holds the door rod to the hinge was not present. | 2 | Mechanical Failure | 97BD4346-351F-4066-930B-640C038DC030
CASE-0487 | Found some condensation in the pans. I got a ladder, cleaned up the condensation, and verified the pans were clean with no water accumulation. I went up to the rack and confirmed all parameters and temperatures were correct; circuit 28 temperature was within range. I came back down and verified the temperature sensor was reading correctly; no condensation formed during this time. There are factors that cause condensation—it is normal for this area to be cleaned daily with hot water, and the store temperature is approximately 20 degrees higher than this area, which is exposed. | 2 | No Technical Fault | B2045699-A1AE-452C-B68F-5D82750307FE
CASE-0490 | Upon checking the case was in defrost at the time the call was requested so upon checking the case is at temp I went up to the rack and found the case to be in good temp and out of alarm with no issues the rack is working just fine then I came back down he told me that sometimes there is a bit of water leak in the sides but upon checking this is condensation fans have already been added and it has stopped the condensation a lot but this case are really wearing of on the insulation and they are dripping condensation from time to time other than that the case is good and doing its job | 2 | No Technical Fault | 6E65D848-E435-4F9A-8B06-6995FEAB18BC
CASE-0742 | I did make sure that it worked properly and showed the manager to make sure that they were satisfied. | 2 | No Technical Fault | D4EE7E31-90D1-45A1-91B1-4248BA9CC8D0
CASE-0678 | Found issue with wiring cases shutting off when they shouldn’t be. Fixed issue now cases are all at temp all ok | 2 | Electrical Wiring | F59B4A73-2D15-4DD0-8017-A4ADAA272CD7
CASE-0987 | Found the ice maker bin empty and evap iced up and condenser short cycling and iced up. After troubleshooting found multiple problems a bad eye sensors. Jumped the sensors and augur motor start. Deiced the evap and found the pump is also is overheated and open. After the ice gone found a broken hose the water distributor. After cleaning water pump it started and it is making some noise. It can fail any time. Also the R1 relay is bad. | 2 | Control Board Failure | 191D1DDE-94C4-4C7D-9EFE-E302969A7C09
CASE-0602 | Found the TXV bulb very loose on the suction line tightened up the clamps. | 2 | TXV Failure | A7D6062A-575C-411F-AB82-DB35BF6DC791
CASE-0539 | Handle is broken. | 2 | Fan Motor Failure | 6E9CA361-FBF6-4295-B0F8-03CDC6D895BF
CASE-0048 | Traced issue to water damage to cube relay block. | 2 | Electrical Wiring | 6847D1E5-A279-4C52-9222-C33E171FEBFA
CASE-0567 | A 1 1/4” cushion clamp was missing from Rack E discharge line and needs replacement. | 2 | Component Missing | 66F3BDC6-C3EF-444F-B434-5002E04EF4EA
CASE-0569 | West cooler added freon. West cooler needs a new drain fitting. | 2 | Drain Blockage | 9D818168-1550-4A32-86E0-5B99D744695E
CASE-0693 | Found leak at terminal plate on compressor 2B1. Wiring to terminal plate is also damaged. Compressor flat on gas on arrival. Found that first thermistor is bad reading -37. Moved sensor to second thermistor. This is reading correctly. Compressor is now running as it should. All ok | 2 | Terminal Plate Failure | BEB83040-51D9-43C9-AF22-982137348DB9
CASE-0710 | Checked in and found meat freezer self contained unit unplugged. Plugged unit in and watched come down to temp. | 2 | No Technical Fault | F7AA811C-AE5D-401A-9087-0AD48D3EDC48
CASE-0098 | Found Produce WIC S1 @ Temp on arrival. Checked log history, found that the lowest temp the box hit was 36 dgs. Target Temp is 35, currently no issues found. | 2 | No Technical Fault | 741B2F42-E27C-422F-AC5B-CE86A5E12A41
CASE-1006 | Water hose fitting for produce water hose snapped off. | 2 | Component Failure | 58E6F235-42C1-4676-83BE-B2001EE75751
CASE-0587 | VFD had alarm for CP30 which a communication error. Re-landed all the communication wires and alarmed cleared. VFD ramped on and at 100 percent call the VFD through an alarm for OT1 for high amps. Motor is rated for 5.8 amps and it was pulling 8.2 amps. Attempted to adjusted tension but shieve threads are damaged and unable to make adjustments. Need to source a new shieve and will get a new belt as well. Was able to source new sheive to blower motor and belt. Returned to store removed the bad shieve and belt. Installed new shieve and belt. Turn unit back on and the OT1 alarm cleared. Monitored system and unit is operational. Job is completed. | 2 | Fan Motor Failure | EF7222C5-3A75-4F8F-9F16-E482FA1EF19B
CASE-0105 | REFRIGERATION / ALARMS / FSD PANEL @ BRIDGE / REFR SHUTDOWN / Power Surge, everything is off right now. | 2 | Power Surge | 641C44D2-9EEF-4B90-8916-5FE367770223
CASE-0101 | apparently the onsite manager was testing the unit and the alarm tripped but all temps are now normal. | 2 | No Technical Fault | 5FB7E4A6-DCB7-4986-9234-E901CD88E83D
CASE-0703 | Defrost is climbing a little high in temperature. | 2 | Defrost Issue | 2B3AB3DE-21C8-44A0-BE48-7AE483895D6C
CASE-0593 | Found that the chute and control arm is broken and can not reach the sensor to energize agitator for ice | 2 | Control Arm Failure | A93E1E75-84D2-499F-9274-15155B838711
CASE-0595 | The grills were covered in grease. So much grease the returns were not pulling any heat out of kitchen. I was able to remove the metal grills from the return vents and clean. Used degreaser and scrapper to remove all grease from the metal grills. When I removed the grills and the return vents were open the employees in kitchen said there was an immediate difference. | 2 | Drain Blockage | 0B3DDD32-8473-474B-8965-8EA9C9408B76
CASE-1013 | The alarm was for 3 economizer alarms. Was getting 9v when it wasn’t calling for it. By passed the economizer and told unit it did not have one. Unit running cold now. | 2 | Economizer Failure | 7FDFB7EE-2E8F-4EC0-9938-2536D717AADF
CASE-0605 | Ac heat reclaims off do to retro. | 2 | Control Board Failure | 297AFDEE-1B0D-4F61-81CE-387A5AFF8E3D
CASE-0597 | LPC causing some short cycling which is likely causing unit to trip thermal overload. | 2 | Control Board Failure | F893D3BB-92EC-4A08-AE29-40FE4405091D
CASE-0954 | Bulb was broken, went to supply house and bought new bulb and cover for bulb | 2 | No Technical Fault | 32FDC86C-9E4E-45CF-B477-32BDEA082398
CASE-1026 | No issue with defrost. Defrost is in normal operations. Case is running properly. | 2 | No Technical Fault | 11C7D918-B7B6-483E-936E-47203A8137BF
CASE-0627 | Blocked return grill cause of high temp issue . | 2 | Drain Blockage | 15FF74FC-6925-411D-9E36-600F7B748652
CASE-1036 | Found that at the time of the rack going down was the time that EEV 1 would go into auto reset at 6:00am. Verified the problem by forcing EEV 1 into auto reset for 3 minutes. Once the valve was fully closed the superheat on both chillers would drop to 0° forcing EEV 2 to close. This was resulting in the rack to pump down. Noticed the cable for EEV 1 was in backwards. Also noticed there was a splice connection on the cable. Checked the splice connection and the green wire was loose enough to come out of the crimp. Replaced the cable with a spare one that was on site. Found that the plug for chiller 1 EEV was not on correctly, the valve was opening when it should’ve been closing. | 2 | EEV Cable Failure | A49BC4A6-CCA8-4F85-A7E2-AD87454F01BF
CASE-0563 | All cases are working properly. | 2 | No Technical Fault | EECFA727-CB3E-44E7-A3D3-23E7109C7906
CASE-0520 | door did not sound an alarm | 2 | Door Alarm Failure | 71023474-E5AD-4EEA-8A54-F18C3C080887
CASE-0969 | This seal contained unit is pushed right up against some flat plastic shelving allowing no air flow to condenser. This unit needs a minimum of 3” of space behind the unit for proper heat rejection from the condenser. | 2 | Drain Blockage | 6611EB22-ACE9-4691-812B-948E16670EE4
CASE-0966 | After the 2nd power cycle, the controller regained communication with the Data Manager. | 2 | Control Board Failure | 8E2FF7D8-EC07-40B8-894E-B909EBAAE7A8
CASE-0532 | I recovered the charge and weighed it back in to the factory spec of 10 oz, then added 4 oz to account for the non-factory filter drier; after letting the unit pull down, it dropped to 26°F, so I adjusted the dial thermostat and it then satisfied at 34°F; performed a full leak check with no leaks found—job complete. | 2 | Refrigerant Leak | 238940E5-15C0-4FD5-B5CB-A8C8F6E941DB
CASE-0535 | Switch not turning off unit. Took apart and seen that lever for cover plate is worn. | 2 | Switch Failure | D55CCA09-359A-40E6-811D-751A830CD4F1
CASE-0536 | Found deli AC held out by corroded connections between pressure safety switches. Cut out corroded wiring and reconnected. | 2 | Electrical Wiring | BFA8E13C-606C-436C-8BA3-6B4E96C75EC8
CASE-0538 | Tech support given to restart the CO2 rack after trapping oil in the freezer’s evaporators. | 2 | Refrigerant Leak | DC426874-D747-4C96-AC9E-F1710EF2F373
CASE-1011 | Rack F, which had an active alarm for case F1 running high temperature. | 2 | Sensor Failure | C15780CE-F8EA-4D20-8D49-47F003E2F09A
CASE-0937 | Upon arrival had to wait for customer to give space to work on equipment. Once available found no issues temp at 28 degrees. Opened door and allowed machine to warm up. Closed door and unit came back down to temperature. | 2 | No Technical Fault | 945A62DA-3044-4045-AA7D-0544046B73E1
CASE-1029 | Shop from home freezer was at -3 dgs when I arrived. Put thermometer into case and my thermometer is reading at -7 dgs. Airflow is good and evaporator coil is clear of ice. | 2 | Sensor Failure | CD32AC5F-6347-4316-BDD7-CFD010A54D4A
CASE-0552 | The rear cooler holding box blower is very dirty with debris and needs to be cleaned. | 2 | Drain Blockage | A0BBC563-D445-46D6-AE63-A32B4753517B
CASE-0554 | Low temp rack High suction at 20 set point of 14.25. | 2 | Refrigerant Leak | 6BF23B26-3817-48C3-9DAB-021FE72EF5FB
CASE-0555 | S.C HUSS LEFT control value alarm at 68.33 | 2 | Sensor Failure | 2F690192-5C90-4955-9D14-D3FD877F7B96
CASE-0939 | Disconnect was not making contact inside. Opened up and closed contacts with bar inside of disconnect. | 2 | Contactor Failure | D50CF5A2-6310-48FE-9E9C-65B57B13BA43
CASE-0630 | I arrived at the site, checked in with the manager, and located the units; they are currently offline. I restarted the controls, but they did not come back online. | 2 | Control Board Failure | 1DE21BC3-9CFC-41A5-87BD-907CCA9FF3B5
CASE-0481 | Found alarm for rack a device absent from network. | 2 | Control Board Failure | 416AE28E-57A0-4930-BD02-1038D9A731AF
CASE-0564 | Pan needs to be replaced. Pan is corroded and float keeps getting stuck. | 2 | Drain Blockage | 4CFA85F4-E524-4CBA-856D-914156E84204
CASE-0922 | Found both evap coils are clogged and full with water. | 2 | Drain Blockage | 1CCB90D1-5CB9-4B9B-9A6B-C1A2DBE319A5
CASE-0302 | confirmed waf | 2 | Switch Failure | 6A907EE7-3143-44D3-B188-0606083E2D6F
CASE-0888 | Drain pan heater on top is in deteriorated condition. | 2 | Drain Blockage | 8C8B4B80-1B16-4375-B8A2-8E79EA3A2EEC
CASE-1111 | LT 1 blowing high to low. Pulled right head and found suction valve cracked and broken. Replaced valve plate with new spare in machine room. Started back up and still blowing. Removed left head and found rear suction valve missing and all suction unloader pins missing as well. Compressor no good. Will submit for warranty replacement. | 2 | Compressor Failure | 4DDFB6C1-E5DA-46AF-9B50-78831B97B9CE
CASE-0832 | RTUs did not alarm. Supply air for RTU 1 is 54* maintaining setpoint. | 2 | No Technical Fault | 6061CCF4-F72C-40D0-802D-B235892DC037
CASE-0893 | Compressor discharge temp lockout is off and should be replaced. | 2 | Control Board Failure | AEED0916-1716-4922-8387-2F0C2A3BB5C1
CASE-0200 | Half of the case is running warm. | 2 | Coil Failure | 84CB1E86-9F03-4B7B-ABC2-FC6F5B54539B
CASE-0306 | Unit started up, freezer is set for -3 dg. | 2 | No Technical Fault | CC47CA8E-648F-4206-AB66-256C3C6387F6
CASE-0397 | Superheat showed it was starving | 2 | TXV Failure | 83E2ABC3-8BE1-4BAC-8A2F-5E0AEF39977B
CASE-0241 | TXV appears to be restricted/ failed. | 2 | TXV Failure | BD1478D6-E35B-48BE-8436-F65096A98494
CASE-1113 | Water flowing from overflow. Set Cooling tower float to OEM water line. Allowed time for equalization. Exercised tower drain valve. | 2 | Float Valve Failure | 8A5F87A3-659C-40D4-9061-B8C44F57BDBC
CASE-0868 | Suction is in COMM LOSS. All Compressors are also in COMM LOSS. | 2 | Control Board Failure | D8BA18C0-59B0-48AE-9AF1-1707C28FA90B
CASE-0404 | Arrived on site and checked in with SD Dane, inspected ice machine, saved ice for Starbucks, dump bin, cleaned bin, water distribution, condenser, and all the required checklist per Safeway, tested ice machine and all is in proper operation. Notified SD Dane. | 2 | No Technical Fault | E7DC4869-D89B-43B7-8B6D-B1665DB20530
CASE-0898 | All repaired points are holding with zero leakage. | 2 | No Technical Fault | A4911823-FC02-4C91-A4A4-C1CAFE722A02
CASE-0023 | Found a1b pulled. Case has a ball valve on liquid line. Closed ball valve. Changed set point from average to side a as it was causing other sides to drop below -20 deg. Disabled alarm for side B. | 2 | Control Board Failure | 16FCC1A6-CD50-44F1-8EF2-2D1E28A19C2E
CASE-0290 | Job complete | 2 | No Technical Fault | A237D595-4C23-484C-A0AF-5D603D14F406
CASE-0207 | Alarm caused by defrost testing. | 2 | Defrost System Failure | B9B7B6F1-1B15-4224-8868-F62780FB26EF
CASE-0830 | Found RTU 1 compressor was short cycling. Checked pressures and unit appears to have a severe restriction due to exceptional amount of UV Dye in system. High side nearing 600psi and low side approaching 100psi. Installed new TXV pressure switch and filter dryer. After adding refrigerant charge turned on system and checked operation. Unit is operating properly at this time with an operating head pressure at 330 psi instead of 700. | 2 | TXV Failure | A53D0882-8A1F-49C4-9C97-C378B0DD253F
CASE-0900 | Arrived onsite went to server room turned unit on seems to be working fine checked filter on evaporator found it clean went up on roof and checked condenser. good informed manager of work completed. | 2 | No Technical Fault | 7065CFAB-B2AA-4E0F-BB52-4DFAE759C087
CASE-0353 | No Leak Detected. | 2 | No Technical Fault | 2FF18FBB-149A-4AE5-8304-B05E69048C0D
CASE-0217 | I adjusted minimum EEV opening from 0 to 20 percent. I also adjusted max operating pressure parameter from 75 to 150. These adjustments will help with EEV shutdowns. EEVs won’t shut down anymore since MOP parameter has more range to allow higher pressure. | 2 | EEV Failure | 33F36FEC-E18D-41F2-BA7F-287E002E7C18
CASE-0878 | Further inspected and found speed control in exhaust fan not set to 0-10v control. Set to 0-10v control and monitored. This exhaust fan cycles on temperature, if nothing is being cooked this exhaust fan will not run 100percent. This system will cycle on and off TEMPERATURES while cooking. When they fryers/ area is not producing enough heat the system does not cycle on. | 2 | Control Board Failure | DFEC027D-046F-4C0B-A63B-CC3320C839A5
CASE-0817 | Inspected the cooler box and found the box temperature fluctuating between 30–35°F, with a discharge air temperature of 26°F. | 2 | Sensor Failure | 3B61FC4E-7497-4A69-9665-3214F4DDFD44
CASE-0347 | Top door hinge assembly was missing the 1/2” spacer. Removed door and found holes were too stripped out to install larger bolts and 2- bolts were broken off in frame. | 2 | Electrical Wiring | 770DB439-A240-46CC-9C3E-F5B351764203
CASE-0350 | Removed product found a failed Schrader that was blowing out. | 2 | Refrigerant Leak | 9E7CAFCF-615E-4E3E-B83D-D44AABF34CF3
CASE-1145 | Found that majority were closed off and that the office was taped off with cardboard opened up all supply vents and removed cardboard. Found that system was satisfying at 80° put in 4° offset Watch system to ensure it made temp. Break room is no in working order. AC-4 found AC for dumping heat into office and back room and bathrooms turned off heat at summer winter switch at indoor unit. Heat is set point to 71. Put an offset to trigger air-conditioning. It is far too warm outdoors for heat to be serving these areas especially because they are so enclosed. | 2 | Control Board Failure | 49884C22-D7C3-4472-91F0-1A419F507E5D
CASE-0824 | found controller hissing, indicating a leak on controller and/or pinch valve | 2 | Pinch Valve Failure | C941492F-DFA3-411E-9690-2327E7A88AD2
CASE-0829 | Fans were rattling due to aging and case negligence. Case is old, tired, and has not been cleaned in a long time. | 2 | Fan Motor Failure | 79B13DB9-F15D-44C0-B3B1-306EC41FBFC9
CASE-0327 | Replace terminal block for condenser B | 2 | Terminal Block Failure | 666D6644-4900-49EC-9857-D08715E3BC7B
CASE-0825 | Found board 2 point 11 alarming every half an hour for days Input is for current sensing relay at rack disconnect Eventually they discovered that target does not require this current sensing relay to be in the rack so he simply deleted the board and point | 2 | Control Board Failure | 46816AE6-31E8-408F-9713-57532425F7F4
CASE-0321 | I found the flow meter to not be reading properly. The flow meter has failed. | 2 | Flow Meter Failure | 17D80265-9832-4415-BC27-24CC49B8E2EC
CASE-0320 | The cause of the high head pressure was the unit was over charged and couldn't pump the liquid into the receiver. | 2 | Refrigerant Overcharge | F62370CB-D65A-441E-AE34-E4C06A46CEE3
CASE-0237 | Tech selected No this dispatch does not require a compressor; | 2 | No Technical Fault | A30F962C-71C3-4C5E-A401-2D8EBAE47020
CASE-0367 | Found deck pans and shelves collapsed into case causing disruption. Couple deck pans cracked and shelves missing clips. | 2 | Structural Failure | FD6FE7E1-79EC-4975-8BE1-D4FE74FC17B5
CASE-1078 | found no amperage being pulled went up on the roof and verified power at the contactor for defrost found 208 at the coil and the contactor was not pulling in transferring power down to the defrost coils replaced contactor verified amperage was going through the defrost coils and everything is working properly now | 2 | Contactor Failure | B622A423-6184-4F9B-B771-1BD1168A0BCD
CASE-0789 | Both freezer condensers need to be reinsulated. Coolerman door snub closer needs replaced. Freezer man door snub closer needs to be replaced. | 2 | Insulation Failure | DFD37301-1BDA-4763-9A18-84A322147D9A
CASE-0442 | Arrived and found evap working as should mechanical room at 91 degrees and Evap sitting at rack pressure and discharging air 30 degrees colder than intake. That coil is not ment to cool entire space may want to have hvac service out to look at fcu4 | 2 | Coil Failure | 2A513D67-EF29-4D91-A1C2-0A2DCC38EDB3
CASE-1122 | Module is faulty. Replace modular board and condenser motor on rack G and H condenser. | 2 | Control Board Failure | 1D43567B-2D86-466A-8062-FB9A68C1D371
CASE-0855 | Found three door self contained freezer empty and at room temperature. Condenser fan running with compressor overheated off on internal overload. Shut down to cool off. Leak checked found crack on access port tubing brazed to repair evacuated and weighed in 24 ounce charge with R-404. Checked operation freezer now cycling at -4. Billable Repair Self-Contained 3-Door Seafood. Re-brazzed Fractured Refrigerant Line. | 2 | Refrigerant Leak | 6BA08CDE-22EA-43A2-A2C1-385FE8BE84FC
CASE-0470 | Checked Opus, found cases are reading stale data. No active suppression or remodel notes found for Cases. CWO. 260530-000945 | 2 | Sensor Failure | 794F03D4-7AFC-4080-8D57-3A300B67878A
CASE-0466 | Found bad Klixon. | 2 | Klixon Failure | B79DE21C-DFD0-4B59-87EB-127312BC5D1F
CASE-0464 | Found comp 3 with bad esr board. Found leak on rack liquid ball valve. Tightened and leak stopped. Compressor 3 on low temp rack going off on phase loss. Esc no good, compressor 3 on medium temp rack is no good, removed esc and installed on low temp rack for compressor 3. | 2 | Compressor Failure | 76E66368-D0A3-4C1D-856E-7693663A6928
CASE-0757 | Kvq not closing will return to restart | 2 | Contactor Failure | FB4C0FA5-38AE-4BD8-81F1-16D5F5F30EDE
CASE-0759 | It looks like the ESR had gotten stuck on the almost on the closed position. Reset the ESR board and temperatures came down no alarms currently as I logged the rack. | 2 | Contactor Failure | AACA91AC-305C-4421-BE24-10A3750437EE
CASE-0169 | Found Rtu 27 not running and appeared to be unit that supplied room. | 2 | Compressor Failure | 9BAD2E4A-3EB2-4D0C-8B69-2588C620C901
CASE-0451 | Found that the cooler and the freezer or both reading high temperature. Went inside, finding all evaporator fans to be running. I went to the rooftop, finding all three condensers were running at this time along with temperature dropping at the cases. | 2 | No Technical Fault | 3DB4568C-3E1B-4907-B1A1-92B1C0D7C86A
CASE-0445 | Found defrost module burnt up. | 2 | Defrost Module Failure | 19856B51-FF1F-4F68-AE2E-CCEFBAA4A93A
CASE-0271 | I located melted starting component parts. | 2 | Compressor Failure | 293BCC16-1E6D-4B5B-90DA-2F0B6348D0C5
CASE-1132 | Replace bad VFD with new and program it as needed. | 2 | VFD Failure | 96518949-6266-445C-9B89-9217CD36940E
CASE-0439 | Found inverter failure for A1 comp had bypassed cleared . EMS reset . Rack now marinating suction setpoint . Alarms clear | 2 | Inverter Failure | 214A146D-73BE-48A5-9DB8-B44993B4499D
CASE-0009 | Found case was coming out od defrost never high temping. Did found dopr not fully closing. | 2 | Valve Failure | F46241A5-B021-4352-A7C9-CB4D28773DBA
CASE-0763 | Proof failure was caused from liquid flooding back to the rack. | 2 | Refrigerant Leak | 84C86884-626D-49BD-8DBD-4C7009AC7DB4
CASE-0335 | Call for RTU-11 making noise. Called FMOC to put into test cooling to see if that’s causing the noise. Fan started, no noise. Compressors and Condenser started. No noise. Went to sales floor and couldn’t hear it. Notice RTU-7 right next to 11. Had FMOC put this unit into test mode aswell to test. Didn’t hear a noise off of this unit either. Couldn’t recreate sound. Call is complete. | 2 | No Technical Fault | B7ED9B5D-CD04-435C-9768-624E1360F8C5
CASE-0279 | Fans running but no compressor | 2 | Compressor Failure | ADB7D671-C0BB-475F-8A05-93817ED6FE5F
CASE-0280 | Checked and found pressures set a little high. | 2 | Refrigerant Leak | 43968A1F-E26B-44D4-AD2F-AFDDEDE6604B
CASE-0418 | Made contact with All Racks and verified all operations are back online expect Rack 4 which has a REF 4 Box connected to Cat 5 on E2 damage, Notified FSS of current damage part and Will need to be replaced with Publix IT . | 2 | Control Board Failure | 78F59AFF-F367-4E5D-8E63-7FF0BA79F024
CASE-0278 | Case does not reach temperature | 2 | No Technical Fault | C0C10BE1-83BA-42EA-93E4-2A420A382FC6
CASE-0768 | I found that someone had hooked up the vacuum line to the Evac motor the wrong place . I moved the line and opened the valve and the pressure held . | 2 | Electrical Wiring | 607F2189-5DE6-45E4-AA28-C60D5A084B81
CASE-1068 | I located the case light and found that the screw securing the light bracket had come loose. | 2 | Electrical Wiring | F449C9B3-4E57-4C0A-A980-ABD3417C3F7D
CASE-0771 | Located service daily case with broken snap in outlet. | 2 | Component Failure | D79D8F1E-89F3-46A2-B8FD-9F95DD05A574
CASE-0964 | Found ice buildup in back right corner of prep cooler 1. Prep cooler butts up to the back of the bakery freezer. The gap between the two has ice buildup. | 1 | Drain Blockage | 7AF03585-0104-4503-AA63-46D2FD8E522D
CASE-1185 | No issue found with air door | 1 | No Technical Fault | 202860B4-FDC2-48B1-918A-1493FA0CBBDC
CASE-0877 | Upon arrival, I met with meat manager Justin then went to the rack 1 motor room and found rack 1 Circuit 1 is currently -7 degrees. All compressor's are operational with normal operations. I then pulled a temp log and circuit 1 started pulling down from medium temp after adjustments were made to low temp after defrost at 18:00p.m. and about 1:09a.m. that when case reached setpoint temperature at -6 degrees. Bunker case is operating normal at this time. | 1 | No Technical Fault | 48EB687E-A2F4-4E48-AC17-58ED257F8D06
CASE-1184 | Checked sandwich bar. Hot air washing out case from Dei mau. Found this day prior. Serviced unit. Cleaned sump, replaced pads, belt and failed float, replaced broken water supply hose and started. Cooler air now but still washing out case. We will need to add another vent and change register to reduce velocity and change air direction. This is magnified with hot weather, turned off mau and labled breaker. Opened store outside air and secured with screw it was 100% closed | 1 | Fan Motor Failure | 4C7A910F-3F58-4A3C-97E6-797676C41670
CASE-0861 | No ice build up | 1 | No Technical Fault | FCAF87CD-FCB4-432D-917C-9C03DF3A581D
CASE-0856 | Inspection found the misting system controlling a case farther down the line was leaking water at a steady pace. | 1 | Drain Blockage | 9CFEF88B-5370-45C3-B802-830E15988173
CASE-0973 | Check with manager, they weren’t aware of the call, further check call is dated 5/18/26. Check case, good airflow and at temperature. Leak search all frozen cases, no leak to report. Case is running properly. | 1 | No Technical Fault | FF5C2ECB-0E31-4854-9F3C-22D28A538DF7
CASE-0862 | Found bottom drain pan element was bad causing short to ground causing breaker to not be able to be reset. | 1 | Drain Blockage | 1E878F8E-B45B-4638-94C8-D961EAA8DEFD
CASE-0865 | Found klixon came off pipe, reattached. Found the activator for the evacuation was broken. This broken item would keep the cases drains from draining. Two coils at this point will need replacement. They are crushed and twisted. A11A and B9C coils need replaced. B9C has a bent lower rail where the door is attached that was causing two doors to fall out of the frame, asked the office to send a carpenter. The carpenter came and adjusted the frame to help keep the doors in place. he has determined that the Ice built up inside the frame and shove the frame downward. | 1 | Evacuation System Failure | 7845B870-7203-4552-9739-1915698CD462
CASE-0968 | The temperature has remained normal with the reach in cooler at 38.5 degrees and the freezer at -1 degrees. | 1 | No Technical Fault | 500455D2-50AD-465D-B356-064F31F83CD7
CASE-0875 | Upon arrival, I met with manager in charge sly, I then went to front computer room and its 72 degrees inside and back room office is 73 degrees matching setpoint as well. I took pressure as well Low:127psi, vsat:43 degrees and High:321psi, and Lsat:100 degrees and return and supply temp is currently 77/55=21 degrees. Compressor and blower motor is operating at manufacturers amperage as well, i then checked reversing valve solenoidand its energizedwhile being called for. I then went back inside and checked inside drop celing vent and its open with no restrictions, do not see any issue with this unit at this time. | 1 | No Technical Fault | 758ED998-26FD-481A-B0EA-2AAAA3AF3EC8
CASE-0967 | I went down and disarmed the box and it was full of water, I dry it and cleaned it, I cut the wet cables, I went up to the rack and the temperature was fine, I went down and adjusted the box and the sensor and left the circuit working and in temp. | 1 | Drain Blockage | B8386813-916C-4CAD-AC72-536A61EBF7FF
CASE-0874 | I ended up calling PSE at 8 pm for an update on the power because all other power for other businesses and stop lights were working, but PSE had no reports for power outages. Within about 20 minutes a PSE electrician had shown up and checked the transformers for the store and found one of the them had a phase loss so the store was running on only two phases and the transformer was bad. | 1 | Transformer Failure | E0196637-A903-4459-959C-01B52036709A
CASE-0873 | Water tower has small leak out of access door. Tried tightening it up door was bending and still small drip. | 1 | Drain Blockage | A4181C1E-C6F9-4AAB-B9B0-73336886E9EE
CASE-0956 | Found P trap behind case appears to be kinked. | 1 | Piping Restriction | 09732BE8-66D3-47B7-B052-A5B5A9CD6841
CASE-0957 | Was coming from the demand cooling valve at the compressor rotolock. | 1 | Valve Failure | 58313C10-1CB1-4A80-9FA1-F87C185522FA
CASE-0859 | Sealed the doors on AC 5 and the ERV unit that water was able to enter the units. Both units passed the water test and this call will be closed out. | 1 | No Technical Fault | 4E9204BB-3830-44C5-A4A0-417A10FD86F0
CASE-0959 | Circuit F cooling has hot liquid and warm suction, need to investigate further. | 1 | TXV Failure | 4AC45266-C4C2-4C4E-8153-033F156A34EC
CASE-0871 | Determined alarm parameters were set too aggressively for normal seasonal operation, resulting in nuisance alarms. | 1 | Control Board Failure | DFF3915D-699E-4F4F-90B9-2A8F126E6A04
CASE-0869 | All compressors were running, all circuits were at set point, discharge and suction pressures were within set point parameters and no alarm on the E2. I stayed and observed rack-4 for a while, no issues developed, while observing the rack, I leak searched the motor room and the condensers, at 0 PPMs, Moving to close this work order. | 1 | No Technical Fault | 91ED132E-2958-4CE4-9FC1-CCD259124DBC
CASE-0960 | I checked the "door open" duration log, inspected the TXV screen, and found that the power head bulb was missing its insulation. | 1 | TXV Failure | 8405E456-0DE4-49CC-BE69-110AF38029B9
CASE-0867 | Compressor 21 is for one of the dairy evaporator coils in the walk-in was alarming for no amps/mon proof because temperature was satisfied from system 17 which is the other compressor for the other evaporator coil in the dairy walk-in. Ammon made some adjustments to keep compressor 21 on. | 1 | Compressor Failure | 1533DE46-BD17-46A5-94A9-ECECBE23B8E3
CASE-0971 | Found heat tape source in adjacent freezer and Ohmed out. Heat tape ohms out but is barely warm. Taped in pipe rupture and brazed area to seal up pipe. | 1 | Heat Trace Failure | 6DA33569-BF37-45F7-878C-401D5C47D3E2
CASE-0870 | Unable to successfully deice will need to return to complete . | 1 | Drain Blockage | D2CD8EA8-693B-494D-9ABE-1A50491B33ED
CASE-0860 | Pharmacy is also not feeling cool due to being right next to the main entrance/exit doors. Heat is more than likely traveling to Pharmacy causing them to not feel as cool. But entire pharmacy room is receiving 65*F and AC3 is running accordingly. | 1 | No Technical Fault | 97AC204C-51A7-4AAF-B27C-38AEEEB140E0
CASE-0961 | Replaced fitting complete . | 1 | Refrigerant Leak | FA2127B7-00FA-4A49-9473-A2CADC950826
CASE-0962 | Found both compressors had lock out modules, checked across lock out modules, and was receiving 24v across C-SI indicating compressors were tripped on a safety but modules were not blinking to indicate that as they should. Checked across all safeties and none were open. Verified modules were receiving proper power and were calling for cooling. Found compressor lockout safety modules not receiving signal for cooling. Traced signal voltage back to economizer. Removed plugs for Y1/Y2 and jumped out plugs. After plugs were jumped out stage one kicked on, but LSD for compressor 2 was flashing red indicating a safety was tripped. Checked across safeties but didn't find any open. Jumped out module and compressor kicked on. Will need to order replacement economizer module, and new LSD for compressor 2. | 1 | Control Board Failure | 238743ED-68E6-490C-BC21-7C839955F5CB
CASE-0866 | Changed evaporator and condenser on walk in cooler | 1 | Component Replacement | 48062B68-4E50-4EB5-AE08-314AA041E9F7
CASE-0945 | Found that ice buildup was due to a torque gasket. | 1 | Gasket Failure | 9DD3C19D-9811-49C9-BAD5-D396DC386A59
CASE-0953 | I was already on site and I started hvac pm. Checked all ac units and tested for cooling. Verified blower motor belts and filters are in good condition. Will need to quote out AH1, AH2, and AC-E to replace parts. All other units are cooling properly at this time. | 1 | No Technical Fault | 5041C5C3-3E94-4458-9A95-0B1D1853D193
CASE-0930 | Returned to replace sc3 on mtc04 dairy cooler and lcd display on mtc rack. Both are now installed and working. All ok. | 1 | Control Board Failure | 70B6CE24-57DF-4792-8372-786786C8DEA3
CASE-0936 | Found that the unit two was alternating between sales freezer and kitchen cooler As if it couldn’t make up its mind which one to monitor | 1 | Control Board Failure | B5E10B54-8B67-42B8-A7A7-41BEDCFF5122
CASE-0899 | Board is bad. | 1 | Control Board Failure | F18491DC-8AB5-4D84-AFD6-1CC1ADDA45FD
CASE-0935 | I shut down the coil one at a time and cleaned all the fan guards. I put them back and started up the coils and checked operations. | 1 | No Technical Fault | 63A80366-1EDF-4DC8-AE8C-E2375F3098FA
CASE-0901 | When I arrived meat prep D16 case was at 45 dgs. Meat prep is set for 45 dgs. Evaporator fan motors are all running. | 1 | No Technical Fault | E38D86CE-BBD0-43AD-83BD-E16DB61A62C3
CASE-0903 | Oil bucket in motor room cracked and oil leaked through floor. | 1 | Drain Blockage | F717856D-1571-41C6-8D8A-039A17B2A6BB
CASE-0933 | Found TXV all the way open. Found TXV all the way wide open. | 1 | TXV Failure | DD4CB465-706C-40F7-8FAA-8295723A3417
CASE-0932 | Found cases were back at temp. Graphed out history and found last night that protocol I experienced high discharge. | 1 | Compressor Failure | 67A14035-002B-40A6-A04E-8780760C6A61
CASE-0905 | Adjusted glass. Unbent clamp that was hanging up on 3 windows. All set. All 4 windows sitting flat at this time. | 1 | No Technical Fault | 0CFEC5EF-6B6C-41AC-A672-66020199AE35
CASE-0907 | Corelink is dead. | 1 | Control Board Failure | 76F9D1C3-3B8F-4107-8F9A-27E9E6B72D48
CASE-0931 | Found compressor alarm cleared it alarmed 3 times and reset itself today off for a few hours during the day before resetting found motor room air intake doors still closed from winter time. Opened doors and louvers will follow up tomorrow afternoon to check on compressor. | 1 | Compressor Failure | 2D7FBF08-BE75-4688-A881-4B2B631D1918
CASE-0908 | Unit is warm and comp is short cycling. Checked start components and start cap tested bad. Replaced. Unit still with same problem. Power cycled and now dixell won’t come on. Dixell is probably bad again. | 1 | Control Board Failure | 99C710D8-3DC4-40AB-B853-BBF455B8B787
CASE-0912 | I uninstalled the left side panel and found the leak at the expansion valve power head, confirmed with bubbles as well. | 1 | Refrigerant Leak | 933BEDAF-A5F3-4370-8049-11F5FC646136
CASE-0879 | Found electrical box loose on the wall. | 1 | Electrical Wiring | 13E1701F-97EC-4235-BB62-BF5492CA7066
CASE-0929 | The medium temp cases came right back on but the low temp would not start back up, had to bypass the shutdown on each evaporator to get freezer and meat cooler down to temp. | 1 | Control Board Failure | 025D4CE5-8948-4C6B-86F9-774AD428D1EC
CASE-0913 | REFRIGERATION / REFRIGERATION / CASES / TOO WARM / All Refrigeration down not working. | 1 | Refrigerant Leak | C304296B-7CA3-4E7D-A29A-43391814932D
CASE-0927 | glycol leaking out of the pressure relief valve, which was not fully piped to the drain glycol is leaking all over the pumphouse floor spilling down into the store fix strain on piping reset pressure control relief valve. They will have to replace it when they replace the condenser. | 1 | Pressure Relief Valve Failure | 98062121-2B83-4D22-8D8A-7EB5CB882273
CASE-0926 | Found unit is R12 and has no Evap coil in it. | 1 | Coil Failure | 3367AFFB-666E-404D-9AA4-71CF2D378718
CASE-0925 | In auto mode system pulls down colder until probe temp reached and then it beeps until door opened then goes into defrost and buttons don’t work until defrost over ( coil reaches 40 degrees) then beeps. Then it can be shut off. | 1 | Control Board Failure | 9A880FC6-EDA9-4132-9E3C-30AD15DCCCE0
CASE-0924 | Found unit had lost its programing. | 1 | Control Board Failure | 4D7F7E5B-EF0E-478A-99A4-DCD85C70978B
CASE-0916 | Confirmed compressor is not grounded and confirmed start cap is good. | 1 | Electrical Wiring | 223864E6-BC63-4BF0-8AF4-175A2478E360
CASE-1180 | TOC verified RTU-1 is not operating properly at this time. Cooling with a DAT of 67. | 1 | RTU Failure | E1B7CDF6-5D81-4256-8646-ADBF700CC7B2
CASE-0917 | Unit 19 and 20 Condenser is in poor condition will be an issue in ambient over 80 | 1 | Condenser Failure | FCD8BEDD-A364-41E5-90EF-8058F3855377
CASE-0974 | Found EPR pressure at 28PSIG. Adjusted EPR to 11PSIG. | 1 | TXV Failure | 45377697-5DC1-4636-AF65-8043B3839A24
CASE-0923 | I noticed water in the C racks main disconnect | 1 | Drain Blockage | BF2BE115-7595-4C75-AE1F-09343FF951C2
CASE-1179 | Found a bad overload protector that broke off compressor. Disassembled starting components and checked. Both capacitors have proper mfd specs. Troubleshooting relay and found to have too low ohms on coil and heat damage on back of relay. Compressor is less than 2 years old and unit itself is 12 years old. Unit is very rusted. We have replaced overload a couple times now. Recommend replacing this unit entirely or replacing compressor again. | 1 | Compressor Failure | 2725B344-55BB-4AE7-8E7B-BFC56EA8E87F
CASE-0897 | Compresor D1 needs to be raplaced. Compressor and safety components on site at refrigeration cage. | 1 | Compressor Failure | 51424996-629A-4E27-A9F0-B823ED5DC023
CASE-0896 | Only issue found with refrigeration PM is damaged door handle for beer cooler reach in door. | 1 | No Technical Fault | 6EDCF015-F8E0-4374-AD38-D30C33B7BE51
CASE-0895 | RTU #2 Lennox unit. Outside air filter fell off. Also missing bracket that holds the filter up. | 1 | Mechanical Failure | 516AB040-1C21-4DBF-94AF-372186189549
CASE-0951 | Checked over operations and found t stat bulb not attached properly to lower coil causing it to run non stop. Reattached bulb and allowed to run. Case now operating and cycling properly. | 1 | Sensor Failure | 2ECDBF8D-34F4-4D4B-91E5-126A7D8A88F0
CASE-0950 | Had UU fault on all 3 VFD. Checked incoming voltage and have 208 v to all 3 legs. Should be 460v. | 1 | Electrical Wiring | BD89C466-F7AC-479F-ABB4-B04E697E74F8
CASE-0949 | Found rubber mats covering the discharge air openings. | 1 | Drain Blockage | 1A4BD639-19E0-49D5-9F6F-AD629E2734EA
CASE-1183 | Removed a motor that fell off of the mount due to stripped screws and a broken fan blade. Condenser coil so dirty we were only able to do 1/3. Will need to follow up to finish as the cases were getting warm. | 1 | Fan Motor Failure | 48342D88-94D9-4088-9294-9241915215FB
CASE-0948 | The noise is coming from the glycol pump. Checked and confirmed pump is operating. The noise comes and goes as the sealed bearing are making the noise. Pump will need to be ordered and replaced. Pump is working and just noisy as of now. Glycol pump working properly and quietly. | 1 | Fan Motor Failure | 12341627-5651-4B8A-8F8A-A6CA6943D99F
CASE-0947 | Found that dial was not operational. | 1 | Sensor Failure | B25F5845-287E-477E-BB66-DCF84CD2EAD8
CASE-0946 | No issues with spot merchandiser. | 1 | No Technical Fault | E08E0FDE-832B-413B-8440-967911D3D944
CASE-0921 | The check valve on the return line from heat reclaim has gone bad. | 1 | Check Valve Failure | 4CB99410-A60A-42B5-AF22-350B55E03D30
CASE-0944 | Removed new bunker from pallet, plugged in and verified coming down to temperature. | 1 | No Technical Fault | 32657836-38B4-4C6B-A455-465D476064FE
CASE-0882 | I found it set at a 60-degree angle, resulting in improper airflow. I adjusted it to a 30-degree angle, and there is now adequate airflow. | 1 | Damper Failure | D1BA1C95-3F22-4D59-A915-82DBFC0CA982
CASE-0884 | Checked RTU-9 found blower motor and pulleys functioning normally it appears that recent repairs were made pulleys in good condition. Checked operation of unit no problems found. | 1 | No Technical Fault | 4D9185DA-76AE-4954-922C-CE68CEF26E30
CASE-0885 | Solenoid on D6 EPR is fried, closing valve. | 1 | Solenoid Failure | 81B088D8-73D4-402A-A611-3C8B61628CC8
CASE-0886 | Suction line frosting up. R22 system 25psi on suction. Could be either low on charge or flood back. | 1 | Refrigerant Leak | 63FF1BD1-BE7B-4310-9F10-51E2475F342D
CASE-0887 | Found air handler unit not operating properly. | 1 | Air Handler Failure | 49373242-98F8-44A5-9668-2A4498F15252
CASE-1181 | Units are not making ice due to having no water supply | 1 | Drain Blockage | 956AC580-AA2E-4811-B0E9-E8FB08A886F2
CASE-0942 | Found the ice machine pulled apart and the water pan dropped down. | 1 | No Technical Fault | 5841704A-47BA-4B3F-83BC-ECAF0A86345B
CASE-0941 | No problem found unit within 2° of that point also EEPR valve is modulating like it should be in liquid header temperature satisfactory | 1 | No Technical Fault | 4B5B4239-1C94-4E0B-A0C5-1E2004F0FCF6
CASE-0889 | Checked case found misters are working tubing was reconnected last week. | 1 | No Technical Fault | 38276F5F-7FB2-48EA-B47F-2AADBF25FFEA
CASE-0890 | Inspection found oil leaking out of the gearbox by the augur. | 1 | Fan Motor Failure | DC1E862C-B409-4924-AE1D-E8A872DD38B0
CASE-0891 | Sentronic is tripping pre maturely. | 1 | Contactor Failure | 3058140D-0FD6-4451-9B03-4958732FC319
CASE-0938 | Fans Out in POS Small Freezer | 1 | Fan Motor Failure | 46720B7C-845A-4251-B179-9BD871891B41
CASE-0892 | The GFI is rated for 5 µA per the instructions for the heat tape. It needs to be 30 micro amps | 1 | GFI Failure | B5ADD3DD-805E-4D86-A50B-143215CF430D
CASE-0894 | Rack A has 6 dry rotted discharge line Kush Clamps •1-1/8” size -Rack A has 1 dry rotted discharge line Kush Clamp •1-3/8” size -Rack B has 5 dry rotted discharge line Kush Clamps •1-1/8” size -Rack B has 1 dry rotted discharge line Kush Clamp •1-3/8” size | 1 | Refrigerant Leak | 6B67CDB4-D0B4-4ECA-8F1C-4C33DB18106E
CASE-0918 | Found leak on heat exchanger in box due to corrosion, it has fully rotted out and they are lucky it didn't dump the entire charge. These heat exchangers are obsolete and not put in these systems anymore. Pumped down system. Cut out and straight piped lines. Put into vacuum. No gas added | 1 | Heat Exchanger Failure | 984BDB21-0971-4AED-B15B-2772E75BAF59
CASE-1130 | That’s confirmed ESR BORD2 point2 is faulty, I called Publix RAM got a high password, move system28 stepper valve from point2 to point3(pictures added). | 1 | Control Board Failure | 950D2EF1-6FEC-4CFA-831E-105340B02783
CASE-0975 | Float was seized up and not functioning properly. | 1 | Float Failure | 57EF07CA-E769-43C0-8F8E-355535780B60
CASE-1086 | Ran all units with them having proper temp differentials. Talked to tech support and got all set points dropped 1 degree. | 1 | No Technical Fault | D9B863AC-A3BF-4A2E-A10D-C92AC073F08C
CASE-1082 | Replace Compressor, Contactor, OMB Oil Control, Demand Cooling Module, Demand Cooling Solenoid Coil and Emerson Digital Compressor Control. | 1 | Compressor Failure | 1B069C4D-9F01-4AD2-A6DD-148FE3316A28
CASE-1150 | found out customer was plugging both ice merchandisers into the same outlet, and the outlet is worn and loose | 1 | Electrical Wiring | CBA46CE4-F1D0-4C8B-A95E-DD202778F3E9
CASE-1149 | Found coil with ice in the rear causing no airflow. No issues with the case itself but found air leaks around the vacinity of this case causing warm air penetration and extra moisture sticking to the evaporator. Icing happens every 3-4 months so this is a likely contributor. | 1 | Air Leak | C32D8D0E-9995-4A72-B515-D0A1B1885289
CASE-1148 | Remove & Replace destroyed supply duct off main air handler duct work. | 1 | Drain Blockage | 3A37AE4F-7280-4498-9E29-1AC288E75234
CASE-1083 | Had 12.5 VDC going to the keypad. Looked up manual and found that to be good voltage. Will need to order new keypad. | 1 | Control Board Failure | 8758EAB4-EB85-407E-B3F8-7E7BD3B89674
CASE-1084 | Water leak under case was due to the kick plate. The kick plate’s bottom lip was catching the water and the water was traveling along the kick plate leaking out on to the sales floor. I found that the top shelves on the case are incorrect and are blocking the airflow. | 1 | Drain Blockage | 4B398359-BB25-4ED0-8BAF-A3DCB8D7A692
CASE-1085 | Located the side that was leaking | 1 | Drain Blockage | 0CC2E54D-8F69-4E9A-BB01-B2AF67AE7D77
CASE-1087 | Found oil for rack A heavily discolored. | 1 | Refrigerant Leak | 853E5CDA-110C-45AD-9719-9F1B56AA9045
CASE-1080 | Stage 1 heat has a bad DSI ignition control board | 1 | Control Board Failure | 0643D2BE-95DA-4DDF-A54E-C370310D9C19
CASE-1088 | All TXVs are completely backseated. | 1 | TXV Failure | D9F8CC4B-D902-47BE-AEEA-230A838088AB
CASE-1090 | Found condensing unit at bottom of case not secured | 1 | Mechanical Mounting Failure | 30B0F103-E7FF-4D5F-8301-6AFC80C8660D
CASE-1093 | SOW: A55 T1, T2 & T3 Temp Sensor Showing Value as None on Connect+ Need EMC reset | 1 | Sensor Failure | 208FCD45-DAC7-4527-BA54-3078697FF1D7
CASE-1147 | I found a digital combiner for the walk in cooler door. I programmed a new digital combiner for the walk in freezer door. I added two sensor controls to the program on the E2 controller. I confirmed with IMS that they are now able to see the freezer door open and close. | 1 | Control Board Failure | BC9BAEFA-CFC0-43AF-9BCC-E75EDD18BA83
CASE-1094 | Inspected condenser unit checked pressures fan all working normally, wanted to check evapor felt no airflow in areas customer didn’t want to remove product | 1 | No Technical Fault | D27F9F73-827E-45D1-9ED9-7AF4BB02D357
CASE-1095 | No alarms at e2 upon arrival. Confirmed RLDS system not in alarm. Needs new in-line filter. | 1 | Filter Failure | 1C9DFA6F-A4DC-4329-98E9-D8CBF0F73748
CASE-1096 | determined the power supply is failing. A replacement power supply is needed and will be ordered. | 1 | Power Supply Failure | 7C691831-0C4E-4950-982F-876F11E748A1
CASE-1081 | Adjustments made to circuits has allowed circuits to perform as intended without ice buildup on evaporator coils | 1 | Control Board Failure | E8401AD7-190B-4C09-8F35-78B7E6C8585E
CASE-1151 | Check the room temperature and found the room doesn’t have a refrigeration system in the room (no cooling) | 1 | No Technical Fault | 328CE582-CB50-4C97-B355-0CB22E4E7206
CASE-1098 | Checked in with manager located deli walking cooler system W and leak check the evap coil leaking pump down to zero cut off the pipe suction and liquid pipe and pinched pipe and brazed both pipes and started up the unit and leak check no leak find and monitoring the unit and temp and pressure , waited temp tag a couple cycles , and temp fluctuated some cases ok and some cases temperature fluctuated , when the unit cycle off and cut in took a long time for 18 min , I recommended to adjusted to cut 70 psig I will be following up Monday morning. | 1 | Refrigerant Leak | A9360C05-2688-4579-902D-E64B4BF68C30
CASE-1070 | I removed a damaged 90° copper elbow that had burst. Installed a new elbow. After removing the insulation, I discovered a second burst elbow and a damaged section of the downflow portion of the drain line. Removed the damaged elbow and installed a new one. Cut out the damaged section of copper pipe and replaced it using 3/4” copper pipe from stock on the service van. Installed two 3/4” couplings to reconnect the piping and soldered all joints. | 1 | Drain Blockage | 47A629B1-EEC4-4111-8175-7A752129A219
CASE-1062 | this is not refrigerant, there is condensation coming from light sensor on ceiling of cooler, will need to get electrician to seal conduit to prevent moisture intrusion. | 1 | Drain Blockage | 19004746-4C5F-45F4-B784-6736A390457F
CASE-1063 | RACK COMM LOSS | 1 | Control Board Failure | 805FA028-29F2-438F-94ED-DC05787ACF2D
CASE-1064 | Across suction filters had less then 1 psi drop on rack A Across suction filters on rack b had less then 4 psi drop | 1 | Filter Blockage | BDA64926-EC3A-43D2-A3BE-5AECADE9F6B0
CASE-1065 | Found ac for gas station with a 10 degree split at 85 and 75. Found dirty evap and condenser. Used mobile pressure washer and cleaned both. After got a 30 degree delta at 75return, and 45 supply. | 1 | Coil Failure | A3FD5B87-6EDF-4999-B3A7-8DE1B251294E
CASE-1067 | I did not see any visible mold, but I did see corrosion on copper lines and food and seasoning residual. I went through Salesforce and looked through Files to see if they were any photos. There were none. I asked workers if they knew anything about mold situation and they did not. I called MIC Melissa and asked her about work order and she stated unit would have to be taken apart. I removed panels to coils and fans and I did discover corrosion on pipes. I used a scrub brush and soap and water and removed corrosion and also used sandpaper. I also scrubbed inside of blast chiller and also scrubbed outside of doors and over hinges. I removed bottom panel and checked condenser coil, but did not see any mold. | 1 | No Technical Fault | 7A347CC5-FAFA-42AF-81A8-69D946FBC541
CASE-1069 | Found rack bottom sightglass was fluctuating added a tank of co2, need to follow up and leak check, exhaust fan attached to rack is locked up need to order new fan motor | 1 | Fan Motor Failure | 22F7E5F8-AA34-49A3-AC69-71F222B392A5
CASE-1156 | Further troubleshoot the low voltage short on RTU 3. | 1 | Low Voltage Short | 116DCAAD-3E32-43F6-97F1-BAFBF7BC31EB
CASE-1071 | I pumped down the circuit and found the screen plugged. I replaced the screen and the case came down to temp. | 1 | TXV Failure | 18B5462F-764A-4AE4-AA2C-6DAADF5F809B
CASE-1077 | Pulled up temp logs for the case and found the last time it had high temped was on that day, ever since then, case has been maintaining temp and writhing .5 degrees of each other. | 1 | No Technical Fault | 5CCF7043-16A5-465A-9461-F1E5E8FD9F9D
CASE-1073 | Compressor 5 is valved off due to bad reed valves leaking high to low. | 1 | Compressor Failure | D533B240-4DD0-4667-B2B0-F956CF49D7A3
CASE-1074 | The cause of the alarm was a cart of used ice packs placed in front of the glycerin bottle. | 1 | Drain Blockage | A4D2F0CA-B7B4-4465-8E8B-9E00DED10832
CASE-1075 | We need to replace condensate pump. The existing one does not have enough power to lift water to the top of the cooler | 1 | Condensate Pump Failure | 0ABD09AC-2A95-4EFB-B2F1-BB44A57D4EDC
CASE-1154 | further troubleshoot Exhaust Fan 13, currently not operating. | 1 | Fan Motor Failure | 37AAF0E3-17E0-4B11-BE57-D4EABB3435C3
CASE-1076 | Found both stages of cooling not running, proceeded to roof. Condensing unit disconnect was off. Opened up condensing unit. Unit was full of animal excrement and 4 alive pigeons. System is from 1979 and needs to be condemned. | 1 | Compressor Failure | BC8B3AEB-432D-4832-B5D7-04BE6A63183F
CASE-1153 | Found internals damaged and loudly hitting casing. Turned off breaker. And left OMB 24v controls unplugged. | 1 | Compressor Failure | 6CB151BB-0081-4001-9FA3-2F36A92F5104
CASE-1152 | Water leak from blowers. | 1 | Drain Blockage | D23038FA-5795-4464-8160-FBE7CD0D8E65
CASE-1097 | Ice/snow has built up on the interior of the freezer on the ceiling due to humidity and at the door threshold due to humidity. | 1 | Drain Blockage | F1003715-48A3-4E8D-BB65-D054F8F1778F
CASE-1099 | Motor saver light red indicating its bad. Tested the point and confirmed it was bad. Replaced the motor saver 250 and got rack back up and running. | 1 | Motor Saver Failure | 7878FA91-446C-4494-92BB-373D70C935CC
CASE-0976 | Found the meat prep room at 52 degrees. Checked receiver level and had about 25%. Checked EPR and lowered. Watched prep room pull down. | 1 | Refrigerant Leak | B3EC8EB1-641C-409D-B477-7E0A59AAB911
CASE-1134 | Both variable speed compressors offline with Yaskawa HV600 VFDs alarming for “OV – Overvoltage.” | 1 | VFD Failure | FAA64DCE-FE68-456A-A041-5401FE547FBC
CASE-1115 | Found trail underneath multiple sections of meat wall. Pin pointed the leak to in between where 2 sections meet. Found 1 of those 2 sections full of water. | 1 | Drain Blockage | 18485FEC-8D83-4F2F-8ADE-23BED2652008
CASE-1116 | Opened panel up and noticed a code for freeze stat opened to many times | 1 | Sensor Failure | 708C44C1-7C6C-4768-9239-BDDCF1E5E379
CASE-1117 | Had to do some troubleshooting restored cooling operation. | 1 | Control Board Failure | 0D2892F2-2AB6-4D21-BE29-7D115F125903
CASE-1118 | Found deli 2dr under counter running warm. Upon inspection found sandwich paper blocking coil. Removed paper, shortly after Unit began to cool down. Condenser plugged by deli paper. | 1 | Drain Blockage | F697BF72-E459-443C-BBA9-B041DD818249
CASE-1119 | Pump cavitation | 1 | Pump Cavitation | 2F7FF870-7A76-4EDD-A7B1-6653BF3C2399
CASE-1135 | Faulty dual temp switch. | 1 | Sensor Failure | 68A78397-5FED-4AC7-AD61-D6B5C7063E79
CASE-1120 | Upon inspection found interior push knob to be getting stuck while trying to open door, took apart door knob lubricated shaft of push knob and reassembled back on door, push knob was originally mounted on with three screws upon arrival, mounted push knob with correct amount of screws and verified door is now opening and closing properly. | 1 | No Technical Fault | 08CFAF82-D4F6-4820-926E-B6C66DA78BBF
CASE-1133 | Evaporator blower is in terrible condition. Drain pan deteriorated and the coil is aswell. Tubing is showing and fin is rotting away. | 1 | Coil Failure | 2AFE639D-BC53-4E01-9364-A148A4F235C1
CASE-1112 | Ice machine had a lower water light, wires had gotten lose for the solenoid and water wouldn’t feed, tightened the loose connections and water is now feeding again and making ice, checked out with store mgr Chris | 1 | Electrical Wiring | F93F066A-0EE5-41CB-B86A-802E1C30C0D0
CASE-1121 | While performing for end of maintenance had system shut down to gather readings system ran warm temporarily. Once turning back on system, system began operating properly at this time. | 1 | No Technical Fault | 08083F41-17BA-4524-B1E1-7107A068E092
CASE-1123 | Upon arrival, I met with meat manager then we both went to cooler and noticed the silence button for the leak alarm is damaged and rusty with water inside. | 1 | Sensor Failure | B1812F15-3D1C-435B-B895-0EB9B8B6276A
CASE-1125 | I tested the solenoid and it wasn’t getting power. I went to rack and found it is going through an EMS remodel. I started tracking the board point down for the solenoid and found that the wire had come loose behind the panel of boards. I repaired the wire and the case started working. I also found that the med temp side of the rack was only running on 1/3 of the compressors. I found compressor 7 had a blown fuse on the board. I replaced it with a spare and it’s running now. I found compressor 5 had a bad contactor. I got one off truck and installed it and comp 5 is working now and rack is fully operational. | 1 | Contactor Failure | BF385345-E701-4550-A6DA-18672F05FE77
CASE-1131 | Removed override from VAU1 Pharmacy and returned VAV back to automatic control. Verified VAU1 Pharmacy outputs DO1, DO2, and DO3 all turned OFF and unit no longer actively calling for cooling. | 1 | Control Board Failure | E87504B6-C3F8-4A56-AA94-2E0DF4392177
CASE-1126 | Ice on suction line was the issue. | 1 | Drain Blockage | A1AB0451-28E7-4466-9DAA-D18CB5E639E7
CASE-1127 | Found heat reclaim working as intended. | 1 | No Technical Fault | 1A6D07B2-4908-4606-8747-D4CD656E3F54
CASE-1128 | Leak detector is going off inside unit, must be a leak in the wall piping, not repairable. Unit should be replaced. | 1 | Refrigerant Leak | 6FFAB9A2-1136-4D66-B1BD-A8FBFFB21E12
CASE-1114 | Main issues found with the rack is that the main liquid ball valve is just about inoperable, the valve moves VERY HARD, to the point that the stem may break. Recommend replacing this valve along with adding one on the other side of the main liquid strainer to help with servicing. While replacing these valves, recommend replacing the oil separator filter while the rack is down. | 1 | Valve Failure | A1661017-5B73-43CB-986F-F71D9D515959
CASE-1110 | Center misters was previously disconnected due to cracked mounting causing leaks. | 1 | Drain Blockage | D3C893A5-9DE5-49D6-A5FE-7911B3AFDFA2
CASE-1146 | Found that tubing was being barely held on by pro press fitting | 1 | Refrigerant Leak | 2CC12DEA-E162-4A1B-90D8-857A3238D77A
CASE-1142 | As1 Ice cream freezer circuit running rich. | 1 | TXV Failure | 83CAE402-E245-4085-849D-08F0DDB85B7E
CASE-1100 | I went upstairs and found that they had shut off a (temporary) water line to the condenser; it had been cut by the door. | 1 | Drain Blockage | FDC8DFCA-AC5F-4ABB-AFAB-1162069BC9F0
CASE-1101 | There were times when both went abnormally low, causing the medium temp compressor to shut down. | 1 | Compressor Failure | 608FF97F-0D2E-4D19-9780-62055A427676
CASE-1102 | Controller was found failed after troubleshooting confirmed proper power and network connection, with the unit stuck in “connecting to Data Manager.” The technician verified the communication path by successfully connecting a laptop to the RDM, isolating the issue to the Orbit TouchXL controller. | 1 | Control Board Failure | 455A9AE1-C0A7-4FEE-BED2-7FB32FA297A5
CASE-1104 | Found the unit in clean mode. Power cycled it when it come back on. It started making noise. | 1 | Control Board Failure | E901615E-D19D-4478-A6FC-EB1FE91D11D0
CASE-1144 | Found why the reasoning behind pilot going out. If the flame is off and you open the door, it sucks a vacuum through the burner assembly and blows pilot out. | 1 | Burner Assembly Failure | D207B198-FF5E-40BB-B0D5-1DA07B1D8EDC
CASE-1105 | Compressor one has been disabled in the controller and is waiting on replacement | 1 | Compressor Failure | E17DD225-1CC6-4D78-8D76-2D3BC290E85C
CASE-1143 | The copper liquid line was exposed causing water to drip down and freeze on the rack and floor. | 1 | Insulation Failure | 3B5B904C-D46D-48AC-8794-CA0D91D26ADB
CASE-1141 | Found that A4.03 has not been down to temp in over a week. | 1 | Coil Failure | F89C9A28-3D59-4BC0-B737-5C72A8149539
CASE-1136 | I did find the TXV bulb mounted incorrectly at the 12 o’clock position. I relocated to 4 o’clock. | 1 | TXV Failure | FF5A7977-0654-4840-B2E0-8FCDEC2EFB89
CASE-1106 | B09b groc freezer has a bad novar temp sensor and door seal. These will need to be replaced. | 1 | Sensor Failure | 0BC16C3C-EE31-46F0-887C-1EA9C89FE3C4
CASE-1140 | Located walk in cooler condenser. Powered unit off and removed faulty phase monitor. Installed new one in place and started condenser. | 1 | Phase Monitor Failure | E0E25A74-6686-4277-8376-F3AAD6B839C0
CASE-1139 | Valve coil was not seated correctly. I did use a zip tie to secure EEV. EEV did start feeding and I did see coils of distributor frost up slightly. | 1 | EEV Failure | 03843924-A4E0-42A1-B5E6-B8668CF3AD86
CASE-1138 | Since units are running and not in alarm coach Aric and I agreed this was due to stocking overnight and leaving doors open. | 1 | No Technical Fault | 97C8E8E8-6E0A-41D6-8E3D-027FAC0B90A5
CASE-1137 | All sections were making temperature. | 1 | No Technical Fault | D0E7BAD6-4AC5-48DC-AB1C-F2401A0F28AA
CASE-1107 | System is running as it should no issues found and motor amping out good. Believe system could have been locked out on smoke alarm was on site last night and metal work was being done in store and was creating smoke. | 1 | No Technical Fault | E80F49C4-7724-4FD5-A570-CD271341957B
CASE-1108 | Screw was broken due to people leaning on it. | 1 | Mechanical Failure | F590ABEB-09AF-42B4-9CE2-22DE91152554
CASE-0853 | Checked operations of the air handler unit and its operating normally. Verified both stages of heating were operating. Store at set point. | 1 | No Technical Fault | F54F10AB-3134-45B6-BF6D-565F6795C96A
CASE-1061 | Looks like condenser Vfd is failing temporarily and shutting down. Put Vfd in bypass to allow to run without Vfd failing. Vfd looks new may not be set correctly, checked one motor is a 575 rpm and noticed on Vfd setting set for 1300rpm, so likely maybe some programming issues, but everything operating at this time so best to bypass until Walmart can figure out why the Vfd is failing, Vfd issue or control issue. | 1 | VFD Failure | AE52340C-3D7E-4B66-8880-507E28B1F0A5
CASE-1060 | Refrigerant loss appears related to relief venting during recent power outage event. | 1 | Refrigerant Loss | F2631656-4D18-4C0A-B1FA-4A9449DC5272
CASE-1014 | Rack A BAC condenser LED screen is sun damaged and will need to be replaced. | 1 | Control Board Failure | 0121715C-67E0-424C-84D2-EAEDAEC1479C
CASE-1001 | Replacing VFD | 1 | VFD Failure | 8B0A9158-CE18-4CA5-85FB-BA29119130F2
CASE-1003 | Located equipment and found that the top cover was bent on the right side, causing it to drop down low. | 1 | Equipment Damage | 1C90411C-114D-4F08-BD38-AE06FF0457A5
CASE-1005 | Checked operation of season 4 all condenser fan motors are running. Both compressors are running. Blower is functioning properly. Adjusted set points a little lower for summer. Everything is working properly at this time. | 1 | No Technical Fault | 3404A5A9-7583-48AE-91E9-DDA65B180B56
CASE-1008 | Leak Check and Repair Dairy WIC System A05-B Evaporator coil | 1 | Refrigerant Leak | BAB0E63F-C5AA-44C6-A600-421EC1286C93
CASE-1171 | Further testing determined the pilot assembly has failed and requires replacement. | 1 | Pilot Assembly Failure | 3F26CF37-3771-41B0-828A-CBFA88588A1C
CASE-1010 | I arrived and checked in with owner. I then changed condenser board. I then confirmed it was working. | 1 | Control Board Failure | E94FEF0F-26F4-4374-A271-C4D9470305C9
CASE-1012 | Munters is currently not operating. Munters, I repeat munters is not operational at this time causing excessive build up of ice on coil. | 1 | Munters Failure | 4E753F95-A215-4C76-B12D-8FD5F07FFE7F
CASE-1015 | Checked alarm settings and found that the high temperature alarms were set for 45 degrees on the SC units. Adjusted to 55 degrees as most of the units operate near 40 degrees. | 1 | Sensor Failure | 0FDC85E6-EF09-48E8-AFEE-48186CA5B408
CASE-0998 | Noticed the controller was throwing high temp alarm and high head alarm. | 1 | Control Board Failure | 964E964C-6272-4B3A-A5D4-AAD72E9BB70B
CASE-1016 | Hallway outside of box is very humid, checked rtu24, going in and out off comm loss and causing issues, pml needs to put in a work order for rtu24 | 1 | Control Board Failure | 42A2A106-B73B-4B78-93D4-CE5674FC9B96
CASE-1017 | Fan unit and cycle pressure switch for condenser failed , removed old cycle switch and left off unit has a headmaster on it and doesn’t require a fan cycle switch rewired the motor for direct power and capped old line unit keeps going off on head pressure and condenser is calcified and in desperate need of replacement every year this unit goes off 3 to 4 times for pressure related issues please quote New info attached | 1 | Compressor Failure | B50FC9B3-D136-467A-A63B-D37E6DADFEA0
CASE-1170 | Inspected dairy walk-in door and found missing trim piece on the bottom of the frame. | 1 | Door Damage | 6F769C64-6AE3-41C2-9B09-564F7FACBB30
CASE-1018 | Call was for ice build up on shelves of frozen multideck. I removed all ice from all shelves. This call is complete | 1 | No Technical Fault | 7FC5FFBD-4C46-4C6A-BA8E-33FB4697090F
CASE-1019 | Noticed ambient fans for that section were unplugged. Plugged them back in and case sweat sclerae’s. No more water leaking | 1 | Fan Motor Failure | 8F5EA70B-9958-4432-8AB6-81520DC4A988
CASE-1021 | it was a danfoss issue | 1 | Component Failure | 72F14262-A43C-4BC2-A58C-601ADB05A42E
CASE-1022 | Found rtu23 dehumidifier is not working at all, but calling for ac and dehumidifier | 1 | Dehumidifier Failure | AE6BF416-A137-46E8-86F3-5168AF859CDC
CASE-1172 | Unit needs new EEV , called tech support, tried to add more refrigerant to get suction pressure higher, but was not able to get to where it needs to be, looks like EEV does not open enough. | 1 | EEV Failure | B693C61B-8874-47CD-A0B2-57A068823405
CASE-0997 | Confirmed that new OFC was bad out of the box. | 1 | Control Board Failure | C69FCD61-C9D8-44CD-9081-6372DE296E8C
CASE-1157 | The store humidity had not reach the threshold to activate the door heaters. This is the same for all low temp sales floor doors. | 1 | Sensor Failure | 6D3C0285-D541-406A-BD14-4AA4EBAAE818
CASE-0988 | Found Cover was lost to Condenser Vent. Condenser is more exposed to impact damage that could possibly destroy unit without cover. | 1 | Drain Blockage | 00EE021A-6F28-42E9-B4A1-AFC62DDDEB46
CASE-0978 | System 27. Walk in freezers. They have a Beer walk in cooler that’s down. It needs a condenser fan motor. | 1 | Fan Motor Failure | 471D2599-ED96-4031-A825-D2C97DC7C617
CASE-0979 | Replaced t’stat to managers office and found okay | 1 | No Technical Fault | 9DB5457E-EDA7-4F2B-9CFD-475556BAF403
CASE-0981 | The CoreLink would have to be replaced. | 1 | Control Board Failure | FFE31C0D-C59D-457C-A37E-5CAEDAFD359D
CASE-1178 | Found Heavy debris inside case . Found heavy amounts of mold, Dirt rust and Airborne bacteria, bacteria inside case . | 1 | Drain Blockage | 2A0659C6-1297-4177-B3AE-6546A64AF88C
CASE-0984 | Found suction valves for cases closed. | 1 | Valve Failure | 2AC4A103-199F-4EAB-B83E-0C0C6714E5E6
CASE-0985 | the 12 foot has NO AIRFLOW..case making 32 degrees air in back wall. 50 on top…case has 12 water troughs to be removed just to get to fans…looking thru return air grill we see tons of water and mold…. | 1 | Drain Blockage | 8E2A3139-F058-43B4-90F2-EF62B1CA78FE
CASE-1177 | Found issues on rack with low temp suction probe, low temp possible flood back. | 1 | Sensor Failure | 8C28D28F-E83C-459E-9965-45F16458C0C8
CASE-0989 | Found door clip to antisweats damaged causing spark. Door placed back on frame. No other problems found. | 1 | Door Component Failure | 9B31B736-5F45-434C-9B53-5E8AE08C35AB
CASE-1173 | Found the coil on the reversing valve bad put a magnet on the stem to open the valve and will leave it. Found a two degree differential across the liquid line drier and it should be changed it’s a 164-S sweat drier. Added 7 pounds of R-410A and did find a valve core leaking on the suction line added a swivel tee to stop the leak. After further investigation at the air handlers found one coil installed the wrong way. | 1 | Reversing Valve Failure | D25BDACB-01C6-4849-BD85-65B873F72D41
CASE-0990 | We will need to replace the thermostat on coffin case. Jumped out fan klixon and will need to be replaced asap. Took pressure drop across liquid core and I got a 16 psi pressure drop across core. We will need to replace them asap. | 1 | Liquid Core Failure | 85A9C0DA-4D01-428E-A12B-3E6D8E97B374
CASE-0992 | Unit was off on fault , spoke with trane tech , unit requires td5 display to find out what unit went into lockout on , went through ac system , all working as should cycled rtrm board power now working setpoint 70 degrees | 1 | Control Board Failure | 23E77A9F-5E29-472E-B5F4-132931855792
CASE-1175 | The mounting bracket for this fan motor is cracked and could break all the way soon so it needs to be replaced. | 1 | Fan Motor Failure | DBD7E2F0-8EAC-40C9-A90A-595CDE3EDD85
CASE-0994 | I verified the low-temperature alarm set point and found it configured to 25°F, with the case operating set point also set to 25°F. | 1 | Sensor Failure | 9F30E6C5-08D1-4F6A-8609-7929C0545362
CASE-1174 | EMS issues caused by previous contractor and improper commissioning. Addition of EPR to a system is a modification of engineering and also not covered. Pumped down Sys B22. Added EPR to suction line at rack. Cut out and removed LLSV in case. Pulled vacuum and started system back up. Wired EPR in to rack board control point from old LLSV 22-1.6. Set back pressure on EPR valve to now control temp for cases with retrofit doors. Had EMS change programming to reflect new changes to system. Removed all temp offsets. All cases on system now within a couple degrees of one another. | 1 | Control System Failure | DC71861D-7B25-4EDF-9665-958FE7BF8592
CASE-0995 | Checked all frozen and meat frozen case stores just attentions replaced one torque master and three torque rods job complete | 1 | No Technical Fault | 295EB59C-1096-4B35-B872-7D58D09C182A
CASE-0996 | Found leaks on a shrader: replaced cap and shrader. Found leaks on flare connections of dual pressure controlls. Tightened connection. Added 24 lbs r404a for a full sight glass. Found evap iced up, with 1 fuse blown on heater circuit. Found rubbed out wire. Repaired wire. Deiced coil. Found controller power wire the crimp on wire nut had broken causing controllor to constantly powering on and off. Once we fixed the wiring 8 then stayed runnning and began cooling. | 1 | Control Board Failure | 80619F6A-8BBD-44BE-B893-0C23613E6576
CASE-1169 | Coil icing up due to being right next to the front door. Recommend recommended moving self-contained unit away from door. Site-caused, unit is located too close to front doors causing wash-out. | 1 | Drain Blockage | C4D6A20E-C0EC-46DC-934A-7CEC69F9800A
CASE-1168 | Capacitor bad. | 1 | Capacitor Failure | C145C205-F6C5-4046-9473-55D0DF27F587
CASE-1023 | As I examined the box of it is all over the place, it’s on screws, electrical conduit, the ceiling, the outside of the evaporator. It appears to be some kind of coloring or frosting. I ran my leak detector through the freezer and didn’t pick up anything. There is no refrigeration issue here. | 1 | No Technical Fault | B95959DA-00EF-4B5B-AD50-B07DBBA7C5C0
CASE-1159 | The unit had dirty filters and tripped on high pressure then unit need to get reset by controller. | 1 | Refrigerant Leak | C4E8BEF5-D5A4-4ABC-B9A7-7C8BC83350B0
CASE-1044 | Found the magnetic check valve bleeding by. The freezer is currently at temperature but is pulling down very slowly due to the faulty magnetic check valve. The freezer never went into alarm. | 1 | Magnetic Check Valve Failure | 7BA70497-7EC4-4B96-8E86-10CB79A7CCE7
CASE-1045 | Found system E16 produce cut room running at temp. Graphed out system and system is using off time defrost to shutoff refrigeration overnight when no one is in departments. | 1 | Control Board Failure | E732A204-7024-4031-B144-97740EADE322
CASE-1161 | Found that a distributor tube rubbed out on one of the coil U-bends. | 1 | Refrigerant Leak | A452CD35-0B84-4DB4-929A-8B891ABDBCAA
CASE-1160 | Found when temping unit that unit is cycling between 37-44 degrees . Went through parameter menu and found multiple parameters set wrong . Adjusted temp probe delay parameters back to factory also adjusted differential from 12 to 6 . | 1 | Control Board Failure | 8DB8FB80-F617-4999-9698-05A2F9B260EE
CASE-1047 | Upon arrival, I met with mic James, he informed me that the office is really hot due to computer black data base station inside this really small office. I then put my thermometer inside air vents and its 71 degrees coming out of vent, and the computer data base station is putting out 90 degrees heat inside the office as well. | 1 | Drain Blockage | F0B3A625-B90F-427F-951C-A86753F1619C
CASE-1049 | I placed the gauges on stage #1, and the pressures were within parameters. I then checked the pressures on stage #2 by manually activating it with the switch on the board, and the pressures were within parameters. I returned the switch to its position and checked the heat reclaim on Racks 1 and 2, which was not active. | 1 | Control Board Failure | E7C9B511-1F7B-47A4-B40A-06D0751BBAA6
CASE-1050 | Found cooler in low nitrogen pressure alarm due to coffee line and in line filter frozen. | 1 | Drain Blockage | 39D7CB47-1362-4A4F-8CD3-70C420C89635
CASE-1051 | During inspection of electrical panel, I found overload relay was melted and stuck on bypassing it Multiple items inside the panel were melted After speaking with Howie Tec Support, they recommended replacing the motor as motor did not test good as well as replacing the electrical control panel with relay that had corrosion on it The cause of the meltdown was due to wet ice building up in front of the blade due to a bad squeegee The motor did not overload and shut off due to a bad overload and relay | 1 | Electrical Wiring | 45C6D56F-CAD1-48D0-8960-56E131D6E6E5
CASE-1024 | Found case with two bad fan blades, causing an airflow issue and then noticed the rack is low on refrigerant. | 1 | Fan Motor Failure | 897DDD99-E751-4C01-8F8D-DDC90FC73CCF
CASE-1052 | We have a faulty cat6 cable that needs replacement. | 1 | Cable Failure | CCCB33FB-2375-4EA6-940A-BF0E26219A80
CASE-1053 | These Condensers Are In Poor condition And clogged With Calcium From Store Water, NEED CHEMICAL CLEANING | 1 | Coil Failure | D27C5E4F-AEB1-4925-9E6D-81475E20BC52
CASE-1054 | Found that DHU for that area of the store has several alarms in place with work needed. Humidity is over 65% in the area causing all open air units to struggle maintaining temperatures. | 1 | DHU Failure | 1C519A70-1F93-43A5-B1CF-95B39B405494
CASE-1055 | The amount of condensate draining through a 3/4” pipe appears to be excessive and may require the drain system to be re-piped to handle the load properly. | 1 | Drain Blockage | 60BADC12-D0E8-4725-BBE9-1277EB80D45D
CASE-1056 | Identified small steady droplets of water coming from all four suction line p-traps during the Hot Gas defrost cycle. | 1 | Insulation Failure | E807DE2F-3477-4218-9976-DBCD64696FBD
CASE-1158 | Txv was hard to adjust and did not respond. Valve is bad and will need to be replaced | 1 | TXV Failure | 767EB761-FCFA-49C9-9394-92F19873B202
CASE-1058 | After inspection of chiller, I found alarm for low suction temperature. I verified refrigerant charge of each circuit and restored operations to chiller, verified proper water pressure and operations of CWP. All is operating properly, found evidence of possible swapping of chiller pumps that caused low temperature of barrel. Monitored operations of chiller and all is functioning properly at this time. | 1 | Refrigerant Leak | E9F17CEB-0EE3-468A-A6D7-7F85CE5E0059
CASE-1043 | Found only 6-9 Vs coming in. | 1 | Electrical Wiring | 009E558E-C449-42A4-B2C5-E5AF165AAE50
CASE-1042 | The PAC controller showed the MT suction setpoint at 180 psi instead of the correct 400–415 psi. Adjusted the suction-optimization minimum; cause of the change is unknown. Rack appears to have previously run with insufficient water, HPV wide open, and the Belimo responding very slowly, though all setpoints now look correct. Receiver pressure had been near 650 psi, likely lifting the relief. Added 200 lbs of CO2 to float the bottom ball. Leak-checked the store with no leaks found; will check box tops on return. Found A1B coil struck by a pallet with a severely bent suction trap—needs a repipe quote. Noted ice forming on the LHS freezer door frames. Oil reservoir is hitting the low-limit switch though the upper sight glass isn’t full. Verified suction-optimization settings again. Cases are near setpoint; will return in the morning to continue troubleshooting. | 1 | Control Board Failure | 873E3840-64D9-4264-950B-17B39425AADA
CASE-1040 | I found these cases at or near temp. Was informed that a Walmart employee had cleaned the coils prior to my arrival. | 1 | No Technical Fault | 1E9745A1-1D63-4B6A-82A6-6B90656E6B4F
CASE-1039 | Found both cases very poorly installed, no screws in evap coil. | 1 | Coil Failure | 17D3941F-4D53-42E5-BC13-BEB432F131E8
CASE-1025 | Found Water Supply Valve clogged with dirty water and Closed Inlet and outlet multiple times Cleared | 1 | Drain Blockage | AD27A02A-41AA-4225-AD93-CFF133F3DB65
CASE-1027 | Upon arrival checked in with MOD. Power was restored. Located E2 controller and verified all suction groups were making set point. Head pressure is maintaining. All alarms have cleared. Racks are operational and job is completed. | 1 | No Technical Fault | E6B52623-A1AF-4D5F-959C-310CA0EAD148
CASE-1167 | Found that the seafood case was running at a high temperature. Gauged up the system and found that the powerhead was not operating correctly. | 1 | Powerhead Failure | 5EA5F22B-F90E-4459-A719-7EA44D944F4E
CASE-1166 | Circuit for bakery was also on same loop. Waited until loop was placed back into service and monitored temps. Cases are back in temp call complete. | 1 | Electrical Wiring | 2BB2C2DC-430A-4F5C-B139-97DB2FCE0093
CASE-1028 | Found sys 1 SVMT case with misters shooting directly into product trays. Directed misters down behind trays and will return in the morning to remount sprayers when product is pulled . | 1 | Drain Blockage | B4E76415-6EC0-4851-85D5-26D72CA89A37
CASE-1164 | Refrigerant was added to rack NF yesterday so this was possibly the issue. | 1 | Refrigerant Leak | D5F54C5C-DCDB-42F9-8559-6715543210BA
CASE-1030 | Found lingering odor throughout box. No signs of burnt components. Leak checked box. No leaks. | 1 | No Technical Fault | 8C55E943-6DC6-4689-836D-35C4822AF595
CASE-1031 | Sat compressor 1 is for circuit A7 and A8 riff. A7 riff epr is wide open and at temp and circuit A8 is at temp. Sat compressor doesn’t need to be running and is off at the dual pressure control. | 1 | Compressor Failure | F091610D-EA8D-49AC-BA68-DDECE67E0EB9
CASE-1032 | Upon arrival checked in with manager mark. Assisted tech onsite with repairs. Call complete. Upon arrival checked in with management and proceeded to the dairy cooler and found the B2 coil hanging from the liquid and suction line. I shut the power off to the disconnect and caped the wires in the cooler, pumped down the circuit to remove all the refrigerant from the line set. Waited for back up to arrive and we cut the refrigeration line set and remove the coil. We capped the line set and took the old coil outside and will return to pick it up and scrap it. We will need to crate a quote to replace the disconnect and evap coil. We need to also replace the suction pee trap and check valve as well as the liquid line and drain line. | 1 | Coil Failure | 131A0C5E-F2EF-4AA5-A45A-BFE8955124D4
CASE-1033 | 3/8” water line on filtration system had burst. Believe reason for break was due to the improper material being used for all filtration connections. | 1 | Drain Blockage | 347D5694-FFC1-4349-BA32-29FF6D07F3E7
CASE-1163 | 2.5 GALLON WATER HEATER UNDER SINK IS BAD AND LEAKING. | 1 | Water Heater Failure | D874CD8D-6E15-49A4-9805-EFD3B94C4FB0
CASE-1162 | Found multiple cracks in drain line of walk-in grocery freezer. | 1 | Drain Blockage | 2CAE5A0E-DC8B-40D0-B95E-06BD44853165
CASE-1034 | Found network screws very loose. Power cycled board and it came back online. | 1 | Contactor Failure | 3FF815BF-DC4E-425E-8DF0-47F43C52A995
CASE-1037 | Found system was not communicating and was not reading suction temp or evap temp. EEV only open 7%. | 1 | Control Board Failure | BA7FD736-D784-4FE8-B9C4-6123FD10EB25
CASE-1038 | 4 flashing lights means bad compressor. | 1 | Compressor Failure | CE23A42F-74A5-4F84-BA0E-716287FE735C
CASE-0854 | Found one defective compressor soft starter. Unit operating on two compressors. Temp swings due to cycling rotation. (Stalls with a temp rise when switching to the compressor with defective starter.) | 1 | Compressor Soft Starter Failure | DB3FCB1D-E158-479F-9F31-41F736B32116
CASE-0626 | Inspect and found left end glass slipped on right side. | 1 | Mechanical Misalignment | 485269E4-4578-4006-9256-B9BD0146EF4B
CASE-0852 | Repaired ice flapper in the ice dispenser. Verified ice is no longer spitting out of the machine. | 1 | Valve Failure | 64554A17-82AF-46E2-A531-2ED338232FCE
CASE-0851 | Repair complete | 1 | No Technical Fault | F52BDDC7-9DE6-42A2-8CE7-5A0357083C7E
CASE-0395 | The comp was offline due to a CIC injection system fault, relay contacts open. Need to order replacement CIC injection system kit. | 1 | CIC Injection System Failure | 0236CD64-DC4B-46FB-85FC-06F7CB6BE442
CASE-0396 | replaced with new unit and pulled vacuum to 500 microns. After doing so re energized unit and it began running, and pulled down to 28 (setpoint) unit cycled multiple times before tech left. | 1 | Compressor Failure | A32D789C-0F66-4971-8C69-FEDB1ECC9677
CASE-0406 | Found that the honeycomb vent for coil #1 was not secured and had a big open gap. | 1 | Drain Blockage | 4405A60E-7166-4B5F-8077-6BC361EF6F44
CASE-0407 | All 8 sections have been cleared. | 1 | Preventive Maintenance | 54EB36E4-B18B-4A52-93A4-F2B3D0034563
CASE-0408 | Checked in with mod gained access to roof roped up tools washed tower and greased bearings to tower, racks and tower back online monitored temps pm complete | 1 | Preventive Maintenance | BE1A85C9-C342-4C96-A621-441C826E16D9
CASE-0409 | I then went inside and located where the filters were swapped out the filters and made sure that the AC unit inside was working properly. | 1 | No Technical Fault | 716E50A3-9974-4594-91B5-E96413DE8328
CASE-0411 | I check the transformer, and it has power. I disconnect the unit, reconnect it, and it starts up. I set the classroom to 72°F, and it trips due to temperature and then starts again. The high pressure remains between 207 and 210 psi in liquid, which I observe for over an hour and a half, and it continues to operate. As a technician, I recommend to the manager to replace the unit, as it is very old. Refrigerant R22. | 1 | Compressor Failure | 7CF399AC-C077-44C3-8AFD-3ADD130FFC4A
CASE-0415 | The cause of the alarm and disconnection was an electronic failure in the store. | 1 | Control Board Failure | D8C98F3B-B360-4A91-BEE0-30982D93AACD
CASE-0417 | Found left side CFM was seized | 1 | Fan Motor Failure | 7C5E6BD4-0D92-4594-A979-9184C72FB80A
CASE-0419 | Re moved /re set bypass on condenser inverter. Re started and holding set point upon completion. | 1 | Contactor Failure | D469DCF4-219D-47B5-BBD0-E07A41CDCF85
CASE-0420 | Found alarm for 1/2 tower command out. Called seer2 to get information on the alarm source. After looking through the programming they determined it was a low fill alarm for tower 1. Went to roof and checked tower fill. Drained sump until fill solenoid energized and started filling to confirm operation. Pulled sensor bundle in the sump and cleaned. Seer2 Informed me that the alarm has been fairly constant over the last couple months but clears after less than a minute. | 1 | Sensor Failure | E70C6984-6346-4B17-83C6-EC5BBD06303E
CASE-0421 | Checked in. Found coffin case. Monitored temp at case and at Danfoss controller. All temp were holding in the normal range. Call is complete. | 1 | No Technical Fault | 762DED37-F45A-4490-9605-504F2BF54903
CASE-0422 | The spray nozzle for produce wet rack that the employees use to wet down produce was leaking because the nozzle was loose on the hose. | 1 | Drain Blockage | EF44FEAD-2F5E-42AA-86EA-9701697C2421
CASE-0424 | motor sheave worn on deli prep ahu. | 1 | Fan Motor Failure | AFFB89C2-B371-403D-8648-C9102BE85975
CASE-0425 | Found the VFD alarming "Over current: Auto remote trip lock." Set it to bypass mode in order for pressures to begin dropping, which would slow all case temps to drop as well. It appears there were remnants of fuses and VFD parts upon arrival which leads to believe it had recently been tampered with. | 1 | VFD Failure | 0DBB14CE-DADC-428F-A1AE-E86DF36D5D12
CASE-0391 | this case had continued to run very cold, product is starting to freeze | 1 | Refrigerant Leak | 7415428B-F587-443F-A6EE-B5F4C5EDEB29
CASE-0387 | We looked at it and it was reading -8 degrees and product was frozen. | 1 | Sensor Failure | D28BF53F-274B-4B8B-8713-655529AFB3B9
CASE-0386 | No major issues or leaks found. The flash freezer and 1 self contained unit are new in the deli dept and not on list. All other listed units had filters changed. Belts are good on A/C units and most have spare belts on site. Store is in remodel currently. No leaks found at this time. Only found minor issues that were fixed while preforming PM. 2 glass doors needed torque adjusted, 1 SC fruit case needed coil brushed out, kick plate needed to be set back into groove on glass door run. Seafood ice machine filter had heavy grease build up and had to be cleaned, customer side ice machine (Coke) had hinges falling off and screws needed to be replaced with larger size for top mounts on cover. See photos | 1 | No Technical Fault | 365E60F6-E18B-4F64-BDCA-BBBA77A0327F
CASE-0362 | Per Copeland mobile compressor should ohm approx 1.46 ohms. Need to talk with Copeland tech support about higher ohm readings, I’m skeptical of compressor | 1 | Compressor Failure | B98955EC-9CDA-4B11-ACC8-D0AFADE7033D
CASE-0331 | Hinge bar worn from years of use | 1 | Fan Motor Failure | 585344FA-F9A5-4B22-8A3D-874CFC25BCE0
CASE-0343 | Cases have multiple issues, verified transducer, sensor readings & eev operations. Suspected non condensibles in system as it struggled to pull down past 15 degrees. Confirmed with Hill Phoenix & was advised this case is not installed to operate low temp efficiently. | 1 | System Design Issue | 0164152E-999C-4A1E-A96C-7B43F4D1B742
CASE-0345 | Found a Leak on the shrader valve so began to changeout shrader | 1 | Refrigerant Leak | 1A0544FE-2F8E-42E1-89A4-668DFEBB7761
CASE-0354 | Determined Leak Detector 54 is defective and requires replacement. | 1 | Sensor Failure | 66B3562E-F1AD-40E0-BDBA-06BE8E02DA13
CASE-0357 | Located light inside dairy door coming off due to rivets for brackets breaking. | 1 | Electrical Wiring | 45218149-7E58-433A-BE45-2A0E9BBEF008
CASE-0358 | I noticed that it is located in front of the supply vent which makes it read low temp and shut off the unit. | 1 | Sensor Failure | 605CEF63-196A-495B-8E56-CD8B66216A6E
CASE-0363 | Ac2b split is 0 psi. Needs to be quoted for od unit replacement. Will submit all information to get new unit | 1 | Refrigerant Leak | CD59739E-51E2-41D1-ABDF-217BAD43F1F3
CASE-0383 | I did noticed the middle door was lower than the other doors and I checked the level of the unit and it was unleveled leaning forward. | 1 | Leveling Issue | 40AA5A72-3954-472C-A549-D5306D774F2D
CASE-0364 | A02 WI FRZ is in notice at 12.45 SP is -7.00. A03 Rear Coffin case 3 running at 49.01 and SP is -10.00 | 1 | Sensor Failure | 34F171FA-8F4F-42F1-A6F8-7BE878F51F8F
CASE-0365 | Did find a high concentration of CO2 in the produce cooler using electronic meter. Was able to narrow source of CO2 to bags of Organic Carrots. | 1 | No Technical Fault | 7E627B4D-18E5-41B3-A56C-B70B40E5E43C
CASE-0371 | Once I powered the router back on the temperature started reading correctly and logging | 1 | Control Board Failure | C4EA7B11-CBAA-41AB-B5E1-0B8A845AE164
CASE-0373 | I found that the housing was separated and possible cause of failure. | 1 | Coil Failure | 412EF2C8-834C-46FD-87E5-E545119F63C2
CASE-0381 | Found loose return duct insulation that had triggered alarm. Resecured duct insulation and reset alarm. | 1 | Drain Blockage | 44C76258-492C-455E-90C2-90A87A5932CA
CASE-0382 | On site, inspected DHU 7 and found unit cooling, got controller from DHU 14 and plug into DHU 7, inspected alarms and found no cond 1 and 2 fan run time, called FMOC HVAC and HVAC division is closed, no PML on site, unit is cooling at the moment, need to return to inspect PML tablet or call FMOC HVAC, notified ETL Flora. | 1 | Control Board Failure | 89DE1D33-D19D-4F57-815C-E3748C5D4472
CASE-0430 | Glycol apple case leaking from supply glycol pipe. | 1 | Leak | 4B19318E-2347-45BB-8446-2DFCE921C38C
CASE-0431 | AC 3 Rx HSP '69' to '85', AC 3 Rx CSP '72' to '88' for 5 minutes, failed with no rise in SAT and 0kW reading on power | 1 | Control Board Failure | A2A2A6EE-7BB1-49FE-A4B8-8240C314057A
CASE-0432 | Case cuts out at 28F and cuts in at 37F. | 1 | Sensor Failure | E56A500A-D358-4E82-B531-A55B43B140A0
CASE-0523 | SUCTION PRESSURE DROPS SIGNIFICANTLY FROM CHILLER TO SUCTION | 1 | Suction Line Pressure Drop | 696B02DB-42FD-4DD0-BD89-384A151F5E6D
CASE-0508 | Rare break rotor replacement | 1 | Compressor Failure | 12C49C1E-7FE5-4D08-9D9F-1B1C9C3CF3F3
CASE-0511 | Found Bacharach gas detector led not lit. Found cover was not on the way. Put cover back and went to fire panel. Alarm cleared. | 1 | Sensor Failure | 3D024227-D124-4BA1-B754-B5FCCF32E29A
CASE-0515 | Heat won’t run. Further troubleshooting is needed. | 1 | No Technical Fault | 616270B7-A2B3-4175-915D-A0930232C35F
CASE-0516 | Comp 6 branch board is smoking, turning off as precaution, will replace. | 1 | Control Board Failure | 0AA80B23-64D5-4BA7-8B12-EFAB322E0438
CASE-0518 | It appears that a section of the heater tube has been knocked into and came disconnected. | 1 | Drain Blockage | 05E5717C-3E72-4CC2-B4F5-9C49FC4F3E3C
CASE-0519 | Found seafood misting system had tripped the GFCI and reset to fix issue. | 1 | GFCI Trip | D42FFF36-CE5C-46FC-BB19-BBA77AC19188
CASE-0533 | No voltage to EEV | 1 | Electrical Wiring | 8F5D51C8-0F1B-431B-B215-8CAF844B9FE7
CASE-0505 | The dehumidifier is hooked up to a single run of ductwork off the A/C unit. The way it is hooked up it is not able to remove the humidity out of the store. The dehumidifier would need to be able to pull in air from inside the store not the RTU. Would need to unhook it from the RTU and add ductwork to the dehumidifier to pull in airflow from the other side of the store for the dehumidifier to work properly. | 1 | Ductwork Misconfiguration | CC7A9FE4-40A4-4307-A744-45F84AD21C1D
CASE-0537 | I noticed that the outlet water temp was well over 120* | 1 | Drain Blockage | BC21C461-0051-4EC7-941E-C16FF4783807
CASE-0542 | air the is blowing thru vents is warm air. | 1 | Fan Motor Failure | 6D3E1281-9CF0-46C0-9403-429204CBE110
CASE-0548 | Starbucks ice machine holding water in the ice bin. | 1 | Drain Blockage | 565179C3-1139-466C-8208-26A4659AC4A3
CASE-0550 | ES1 for hvac not in comms | 1 | Control Board Failure | 1C85A4D2-3889-4053-B695-D5BB576AB56B
CASE-0553 | REBUIT FLUSH VALVE | 1 | Valve Failure | 4233C7DF-C8DB-4000-BA9D-09AC15BCC1C5
CASE-0562 | This unit is challenged electrically and needs to be addressed. | 1 | Electrical Wiring | 3F634A3C-1CAB-4F87-A68B-8903AEA45DFD
CASE-0507 | found comp 1 suction filter shell | 1 |  | C4A9D2DF-00E3-4B25-94AF-A268E74B79FC
CASE-0503 | Compressor is broke up and not pumping. | 1 | Compressor Failure | AC6F384C-FE8F-4E84-9B46-2CBDD30C3D50
CASE-0433 | Call on ff cases warm on arrival case at -5 degs good airflow verified with manager on duty all ok | 1 | No Technical Fault | 04A8BE7E-BA44-4BB5-A502-12197DCF565C
CASE-0457 | Power failure related all ok | 1 | Power Failure | 3A18CF34-AD91-4377-AA36-0570DC834D14
CASE-0434 | I found parameter that reads off and on for every day. | 1 | Control Board Failure | 05FC903D-7E1F-416A-AC2B-E16F39B429A7
CASE-0436 | Called watchtower to verify all operations and they said everything was in check and there have been no faults since they were reset. | 1 | No Technical Fault | 4E13C751-6C43-46D6-B96A-9A1D92FE7AD4
CASE-0443 | I found wheel on sidling door missing screw scraping floor causing friction. | 1 | Mechanical Failure | 3071CF34-92C8-4B1A-82BE-FC2FA323B5F2
CASE-0450 | Checked the case and found it running -10°. | 1 | Coil Failure | 084AD5B0-4431-4F12-AFD5-4D58D9C71883
CASE-0452 | Further investigation revealed that the noise was coming from the compressors located above the restroom area. | 1 | Compressor Failure | 3DA08ABB-43B5-489D-B58F-CAD85FF1317A
CASE-0456 | Two Currant sensors wired together giving a low amperage ready. .23 amps. Fans amping out at 6 amps. Called tech support and re configured wires to get correct amperage reading. | 1 | Sensor Failure | 255A26AD-BB7D-4C07-9FAE-6FE9B9219AD3
CASE-0467 | The equipment is liquefying water everywhere | 1 | Coil Failure | 5984A0FB-4972-4480-A79D-B79F3E004A00
CASE-0494 | Found water to be leaking from B10 open air dairy cases. System will continue leaking water unless a larger repair is made. Submitting quote to shutoff system B10, return and reseal entire length of open air coils | 1 | Drain Blockage | EE2E855E-CFEE-4B97-838B-09860D5E7B49
CASE-0471 | Then it went into a defrost mode and allowed it to finished the defrost and then finished thawing it with my little hand torch. Put the racks back in it and turned it back on. Cleaned out my work area. Let it run for a while and then checked it again. Temperature at 20*f now and dropping. With good airflow inside. | 1 | Coil Failure | 8F0D41A2-2383-4E94-A8D0-91C1C937B337
CASE-0473 | The door switch is working properly and fans are now on. Freezer is coming down in temp nicely. | 1 | No Technical Fault | BBA92FE3-2A83-49A6-ACAC-856799ECB118
CASE-0478 | Called Emc and they verified temperatures and per Emc temperature probe is good and was instructed to adjust temperature control and call back in about 3 hours. | 1 | Control Board Failure | 75D66BC7-1ECC-492D-A5DF-DF71AD97CF44
CASE-0483 | Board 10 is in an enclosure just below Bacharach Leak Detector. It is an 4AI/4AO board. Checked its wiring. There are no wires landed on the inputs that are programmed as 10-1.1 and 10-1.2 center and perimeter photocells. The two analog outputs are wired to an KELE board for dimming the lights. | 1 | Control Board Failure | 80AA6605-515D-42AF-9D8F-24D70591665C
CASE-0484 | Sound was described as a “vacuum sound” so I assume it was the activator. Pressed activator button and it worked without issue. | 1 | Valve Failure | AFE7B9B3-70EF-4FDD-A964-24B6DEE95B1C
CASE-0485 | Discharge air of 70f out of RTU-2, is due to cooling and dehumidification operating at the same time. Heat from the dehumidification cycle mixing with cool air from the cooling cycle. | 1 | Dehumidification Cycle | 3AD72921-AF85-447B-B01B-FED16CFC9FE6
CASE-0315 | Found air handler 4 that controls outside air to be running with CT to not be seeing fan running. | 1 | Fan Motor Failure | 9F819E95-5BA5-496C-AFE6-3388E0698EF9
CASE-0312 | Checked case temperature and found it is at 17F. Case specs call for +24 discharge air temp/medium temperature. | 1 | Coil Failure | 36FD4EDE-DBBD-463D-9053-883B3C1DD402
CASE-0309 | I noticed pump 2 settings seem wrong the cut out higher than the cut in, graph showed pump 2 never on. I override pump 2 on and temperature dropped to 34 degrees. Let FSS know about issue and he made me adjust pump settings to cut in 14 and cut out 2. Now both pump working and temperature dropped. | 1 | Pump Failure | 3C84F587-8E81-437D-85F3-5CDDFAF7E981
CASE-0165 | Found produce cooler with small leak from drain pan unit is too high to access will need to get lift and return to troubleshoot | 1 | Drain Blockage | 25F1BDC1-9EC2-49BD-B98C-D96FAE4E94C3
CASE-0129 | While working on air conditioner, found flue pipe to be disconnected. Had Manager put in this work order to repair flue pipe, reconnected flue pipe and glued system operating properly at this time. | 1 | Flue Pipe Disconnection | 73022B41-E562-4730-83DD-91C27C3979AC
CASE-0139 | I then found that ground beef section was running slightly warmer than any other section. I then was able to adjust the TXV to balance that section with the others. | 1 | TXV Failure | 8BAF3DCB-2D85-4AA9-87D9-DC427C615462
CASE-0140 | System 1 was locked out because the cut in/out settings for the LPS were not being met due to the box being colder than the setpoint. | 1 | Control Board Failure | 8AC66A90-3FB9-4390-AE72-75654A236608
CASE-0151 | Found 90 on case 1B had come off. Replaced parts and went to every actuator in the store and actuated them to verify that they were working properly. | 1 | Valve Failure | FD33F169-54DE-4A4F-94C8-97253E0DF3BB
CASE-0155 | the cases at temp only case alerting was CO7A glycol and checked the case the pipe was cut off may leaking | 1 | Refrigerant Leak | 2D47C8A4-11E3-45F1-93D7-2A30BDC47E84
CASE-0162 | replaced it with the site provided compressor | 1 | Compressor Failure | 5BA47290-A5B1-42E6-9FB0-EEF98E472DD1
CASE-0171 | Looked over all valves, filters, and transducers and verified no issues. Good liquid level and all condenser fans are running. While further trouble shooting the store had completely lost power. Couldn’t further troubleshoot into root cause of high suction spikes. | 1 | No Technical Fault | 0D74656B-5D02-4DCF-910B-5597CB9C65C2
CASE-0120 | Found that it’s not Evap leaking. It’s water heater above meat box. | 1 | Drain Blockage | 4AB4A091-E268-4E16-917E-24E813657EFF
CASE-0177 | The alarm on the panel is reading CO2 RACK >> LOW >> 22? CO2 >> STAGE OUT 1 | 1 | Refrigerant Leak | A23712B6-64B6-4CD9-8E2E-FF772A8BB113
CASE-0180 | Mini previous broken screws impeded proper mounting | 1 | Electrical Wiring | CA1CF2D0-C9E6-414A-8114-2F6576EA6AEB
CASE-0185 | I reset MT compressor and it came on. I was looking at the VFD settings and noticed the low limit was 15 Hz I feel that is too slow. | 1 | VFD Settings | C55FC216-5CFC-4309-9D1E-E1D5648AB2A9
CASE-0188 | I investigated the issue with circuit 20b and determined that it was not achieving the desired temperature due to a vapor-locked TXV. | 1 | TXV Failure | E1C9A9BD-FFCB-434F-B455-0F72DB15A662
CASE-0189 | Call for broken top lid bracket. Top left lid hold open is cracked. | 1 | No Technical Fault | 1B786211-16C8-4927-847C-E50278C78C45
CASE-0190 | Produce berry self contain unit running at around 60 degrees and throwing a HA error. Looked up the error code and its high head pressure. I believe the unit went off on high head from being dirty and the pm tech came and cleaned all the self contains. Power just needed to be cycled to reset it. | 1 | High Head Pressure | 9D18A49F-EF71-4F89-95C7-1934BA5C23B4
CASE-0127 | Ice machine power at switch was shut off light red in color. Turned switch to open position ( light blue) and unit began going through freeze cycle. Checked unit operations. Machine went through multi freeze and harvest cycles with no issues. Job complete | 1 | No Technical Fault | 7AF3C5ED-9D98-4701-8931-3994CAEC9031
CASE-0116 | Found that there was debris in the C cup | 1 | Drain Blockage | 18872E9E-1289-40AD-896D-C518853C6C31
CASE-0199 | Found that all 3 circuits flat. Oil stains in each coil. 4 coils total. | 1 | Refrigerant Leak | A58C807F-0C20-4A05-87FD-8AE945A045CD
CASE-0070 | Found that the produce cooler accumulator kept on running and not shutting off. Found that the pressure built up to 20 psi. Cleaned accumulator and sensor hose. | 1 | Accumulator Failure | 9C0F6194-80E6-4C25-BFCF-A5D35BB4C14E
CASE-0006 | Found Hot gas valve in remote on in controller | 1 | Control Board Failure | 557E31B9-47A7-4ED3-99F1-0E99240F0A16
CASE-0026 | transducer is reading correctly | 1 | Sensor Failure | 33A73510-47AE-4CB7-9F5F-6853BF00C129
CASE-0036 | Belts on the seasons 4 roof top unit were squealing. Belts need replaced. | 1 | Fan Motor Failure | A186784E-1B35-4011-922B-302D1CADCFFA
CASE-0041 | The Evap is bad! | 1 | Coil Failure | 5C436DC1-B02E-4C30-B631-4EEBDE4A1604
CASE-0045 | Found 1 unit with comp open on internal. | 1 | Compressor Failure | A6EC1387-C5F9-49BF-B78D-C487270809B9
CASE-0059 | Found normal operation and no leak detected. It does go to soda pumps which we dont take care of. Did found soda on floor, someone must of changed box or a tank esrlier today. Reset alarm and monitor it, never showed up again. It reads 510ppm which is normal operation. If alarm returns store will have to call coca cola or whatever soda procider they use for their pumps as is their machines being monitor for co2. | 1 | No Technical Fault | F8D08E45-47E9-4F95-9206-DF594F9F1AD8
CASE-0075 | Controller doesn’t seem to be keeping up with the humidty at case. | 1 | Control Board Failure | 187D6462-123F-42D3-A20A-B08A69FEF6BF
CASE-0113 | On arrival could smell natural gas/propane smell around area, could not smell it inside or underneath case. Issue unrelated to refrigeration systems, recommended store to call plumber to inspect gas lines | 1 | Gas Leak | 10416D48-2015-4AC1-A8DF-D0BE1E44C0F3
CASE-0077 | Heat is trapped and can’t reject causing unit to run high temperatures and struggle to pull down. | 1 | Condenser Blockage | 5A21E4FD-73D8-4807-8359-C48BB7B8E31E
CASE-0078 | Checked in and found water main had broken for shopping center. Found racks off on high head. Water restored to store. Got racks running and watched cases pull down. Monitored store operating. All cases at temp. | 1 | No Technical Fault | 62ED2659-A414-4312-92C0-E6530E80F73F
CASE-0082 | Figured out the weird noise she was referring to was the acorn system sucking up water as the cooler was in defrost. | 1 | Drain Blockage | 6449FEAE-2208-45B7-9D01-2DB08D5FE2EC
CASE-0095 | unit #1c low on charge. | 1 | Refrigerant Leak | B47A233E-1847-4FAD-A399-AB440489C019
CASE-0100 | Found skid with middle sightglass of receiver bouncing | 1 | Refrigerant Leak | 564E279A-F09F-4EDE-AD8B-29995B845747
CASE-0108 | Found space heater above ceiling constantly running, blowing heat into space. | 1 | Heat Trace Failure | 1D242E70-01EE-43A5-A859-2DB3BD369101
CASE-0196 | LT comp 5 is grounded, manual off. Found that store has Condenser A setpoint temp at 100 degrees. Monitored fans cycling off with discharge above 240#. Called FMOC to recommend dropping setpoint temp below 90degrees so all fans stay on. They refused to change setpoint because suction pressure was within 10# of the setpoint 16#. I explained to them that cases will not work properly with suction pressure above 20# but they would not make any changes. | 1 | Compressor Failure | 9D8689AE-6777-402F-91A3-0A3E6036A409
CASE-0204 | Found that piping on suction side of the evac buffer box was disconnected. | 1 | Piping Disconnection | 54624D39-7CDE-4090-95E5-564FA4CFFD20
CASE-0308 | found it blinking with a error code, went to the roof and checked the outdoor unit, everything was good, checked the indoor unit and found the front plate not moving up like it should, repositioned and the lid is now closed | 1 | Fan Motor Failure | 6920B44B-059B-4A2F-9C37-8768174EE94E
CASE-0287 | CONTACTOR WAS DAMAGED | 1 | Contactor Failure | 16EE583D-0467-4C64-B3C8-B1B1717D7C07
CASE-0268 | The extra time is due to the first set of doors listed on the bottom has a short in it. We need to go through the wiring on the left-hand side of the two doors to figure out why it is not feeding power to the plugs as well as we need to install a new plugs and new pens. | 1 | Electrical Wiring | E79B3230-27F3-4FE1-9972-EE6E6B111765
CASE-0273 | Found that there have been notices for Comp 3 on Rack B for proof fail, however the last notice was dated for 5/31 and only lasted for 5 minutes until it was automatically cleared from the E2. There hasn’t had an issue since then. | 1 | Control Board Failure | 9DEBAF3A-C68A-4BC3-8D24-AF2F903E279A
CASE-0274 | Low center light timer, Generator was tested, the low center lights timer is making lights come back longer than 5 minutes per Cat Generator maintenance vendor | 1 | Control Board Failure | 0F73FEA5-B535-4E40-BA78-0A44E085415B
CASE-0275 | Replaced ecm motor on office ac as per customer request. System is now cooling and temp split is 18 degrees | 1 | Fan Motor Failure | 1BBC5592-24B6-4A84-B9DB-B37953C79AC3
CASE-0276 | Suction line needs to be re insulated and far EVAP missing threaded rod causing EVAP to lean away from drain. | 1 | Insulation Failure | 26912787-0AB5-43E2-AEC7-A4FDF1FFEE58
CASE-0285 | Found that split system was not cooling | 1 | Sensor Failure | 777CFDE4-69AF-4C6A-8EC7-357CE0511439
CASE-0288 | He then noticed that epr was at almost 0 percent but was way over feeding | 1 | Sensor Failure | 5B8DA32E-F665-4D1B-9241-0B108DE19823
CASE-0266 | Found that due to high amounts of corrosion on endloop of evaporator that solder was not sticking | 1 | Refrigerant Leak | 5B6E10F3-45BD-462C-816E-C7EC5CFE16BB
CASE-0289 | Checked system 14 and found all working ok, cases are at temp and have not alarm since, store is going through gas retro fit | 1 | No Technical Fault | C02F9141-56AB-4BD3-A725-F1EB7E47B96E
CASE-0291 | Found each unit had a 4102 error code. | 1 | Control Board Failure | EA01988C-1DDC-417B-88F1-016C7BAF08E3
CASE-0294 | An alarm on (Unit A System Bad modem). Keeps popping out. | 1 | Control Board Failure | 64B064FD-15E6-4992-83D1-33200E4D97DF
CASE-0299 | No amp draw/voltage reading from MT2 as it is turned off due to being diagnosed as bad. | 1 | Compressor Failure | 756D276B-30BB-435E-87A0-F431FFF790A3
CASE-0300 | Found failed socket. | 1 | Fan Motor Failure | 06D62296-4F60-4240-9159-1CEF7D7CAD07
CASE-0307 | RTU8 compressor cabinet needs sealing. Leaks water when washing condenser. | 1 | Drain Blockage | 94181CE5-6A52-4C2D-ADED-73D29CD21BC8
CASE-0267 | Closed valved to come to conclusion bad TXV on rcu C. | 1 | TXV Failure | D5C2C8BE-3401-4095-B9D9-20581A3AC79C
CASE-0263 | Found DAC-35 door monitor magnet mounting brackets broken. | 1 | Mechanical Failure | D1B1AE10-3FC7-414E-B039-801181741A65
CASE-0208 | No issue found. Leak detector was set off due to ongoing compressor change. | 1 | No Technical Fault | D929C537-499C-4F3E-9C28-D0E3B740C714
CASE-0229 | found feeder bypass is open and water is looping through that instead of the cryo | 1 | Drain Blockage | 6DD11FF4-62B4-4B83-B3EC-EDC3AD923694
CASE-0212 | All mods in comm. Cases have been reading the same temps since at least 06/02. | 1 | Sensor Failure | 789BAA21-98D0-4DA7-918F-4BA72AA9199C
CASE-0215 | Defrost confirmed to be functioning properly. | 1 | No Technical Fault | 5E8199E9-5E49-45D0-A390-1FAB14656E4B
CASE-0216 | The walk is box I swelling severely in all corners. | 1 | Coil Failure | D273F6E2-0C78-48A9-BB8E-251F9F7F0F64
CASE-0218 | Found power source to be bad, getting 115v in and no DC volts out and not allowing secondary RO not to run. Temporary wire in main RO and found water constantly leaking out of drain line and on top of case. | 1 | Control Board Failure | AF0F803E-4315-435C-A781-E0A98E4B88D1
CASE-0219 | After reading manual I found this style module needs to be reset. | 1 | Control Board Failure | 5E84EED2-C0AE-4840-9C4F-A9EBEADDB786
CASE-0225 | I accessed the suction group settings and saw that although the suction set point was 43 psi and the deadband was 2 psi, it also had a "float" system enabled where the suction set point fluctuated between 50 and 43 psi. I disabled this configuration and left the rack working with a suction set point of 43 psi and a deadband of 2 psi. | 1 | Control Board Failure | DB4B1F16-FA84-4F23-8A61-B37D7E6BC372
CASE-0234 | Larry - Amazon delivery freezer has bad light bulb. | 1 | No Technical Fault | B3ABB6CF-4764-4C6C-A9E0-D8400AF5F884
CASE-0262 | unit also appears to be older and no longer able to maintain the load of product and the ambient air dumped in after years of dealing with ambient temps outside of its design spec, case pulled down but will continually struggle during hot summer months, heavily suggest we quote a replacement. | 1 | Compressor Failure | C7E28CB2-EAB7-4737-8412-42DB1E65C0E8
CASE-0235 | the old wire has lost communication to the E2. | 1 | Electrical Wiring | 5E50E28B-FB08-4F9D-8B2A-69E7382E4417
CASE-0238 | POS cooler frame has a bad LED Driver | 1 | LED Driver Failure | 5AFEB440-EBD2-4C8C-99B3-DEE34D1DC762
CASE-0250 | Found unit off on alarm due to thrown belt. Replaced with spare belt in cabinet. Unit up and running. Unit has a 46° Supply temp. Quoting out new contactor and capacitors due to ware and a spare belt. | 1 | Contactor Failure | 46E944B5-3E78-4E19-84B6-A33410CDED6B
CASE-0251 | I found the left side stainless steel cover on the associate side missing which is causing the case doors to collapse. | 1 | Drain Blockage | 3054C79F-7713-4A98-B057-46AF0505968E
CASE-0252 | Checked out ceiling and found no A/C attached to this space. | 1 | No Technical Fault | A6684318-3D7E-4615-A485-036A1F022FB4
CASE-0257 | Upon arrival no ball in resevoir or receiver. | 1 | Drain Blockage | 30EA9EF9-A3AB-49B7-9B48-333E6E6FDB9F
CASE-0568 | The plumber they have out here says that there is a crack in unit where the gas goes into the unit. The guy said its a cavern ? Inside it the chambers are cracked so they are going to have to come back. | 1 | Coil Failure | 6C7FF9A5-9E31-45E7-B6E0-815A2F8D05AB
CASE-0571 | Found vents above prep tables or blowing straight down directly onto prep tables. | 1 | Drain Blockage | EDAFD4A4-0996-4DCF-9BF4-979B2B23C0ED
CASE-0572 | Drain line didn’t have a good slope/pitch to it | 1 | Drain Blockage | EB88DA20-021D-4AEA-A5FF-334F6CB5F84F
CASE-0778 | The verbatim sentence(s) retained from the notes. | 1 | No Technical Fault | 6903BC26-3173-4BA0-B15F-8920B01838E7
CASE-0764 | I went up to the roof, checked the exhaust fan and it was working perfectly, removing a large amount of air. I connected my current meter and the motor is drawing between 5.86 and 5.9 amps (the correct value). | 1 | No Technical Fault | D944DD77-42F8-4639-8C96-ADA3A9125FFA
CASE-0767 | Found it showing there was a call for cool but compressor output was off. Contacted Walmart monitoring and was informed that outdoor temp was reading 0°F which was locking out the compressors. They overrode temp to 70°F and unit immediately came on and began cooling. Contacted Novar technical support and they stated that the outdoor temp on ES1 is getting pulled from the AHU’s which are both currently offline. | 1 | Sensor Failure | AE43ABE7-1467-458E-AF47-A62ED1F91093
CASE-0769 | Found circuit 25 with high suction pressure at about 80psi. Adjusted the epr to bring the pressure down. | 1 | TXV Failure | EF8D554A-F2B3-4225-B0A2-AED68B86E077
CASE-0770 | Located glass doors that are rubbing together. Both glass doors are slightly chipped. Door 2 and 3. Lifted doors and was unable to adjust door 3. Noticed big gap between door 1 and 2. Slide door 2 towards door 1 to close gap between door 1 and make room for door 3 to shut without hitting door 2. Both doors functioning properly and no longer rubbing together. | 1 | No Technical Fault | 6CD80FAB-17AA-436F-9BF9-D2E133625262
CASE-0773 | Recalibrated their temp probe and call is complete. | 1 | Sensor Failure | DD95F1D4-0B15-4E32-AE57-1801020D20F9
CASE-0775 | Light was broken due to the product hanging over the shelf, slightly, causing the lightbulb to shatter. | 1 | No Technical Fault | 88AEB88E-66BF-4091-A7F4-60CB49F762EE
CASE-0780 | I found the discharge pressure is running about 20 psi above set point but all the fans are running. I then pumped compressor down and cleaned the demand cooling sensor. I then observed compressor running normally with no other issues arising. | 1 | Sensor Failure | 9EC0E90C-5B97-4E48-AE36-DB35028E9FE3
CASE-0761 | Deice case and push end cap back together and close gap and reseal. | 1 | Case Failure | 6214283C-40F2-4537-8E72-715E1DAE5E1D
CASE-0781 | Confirmed required voltage, sourced motors locally and replaced. | 1 | Fan Motor Failure | CB76B1B8-C0AF-485C-98C2-EC647674DBC7
CASE-0782 | The problem originates from the Tesla generator, which is providing an inaccurate reading on the rack. | 1 | Sensor Failure | 3A2937E4-F9E2-4CE9-A0D4-C1C61EC686AE
CASE-0783 | Inspected unit and found the blast chiller was not level, causing condensate water to pool toward the front of the unit and leak out. Also observed product bags, including grape bags, being loaded in a way that allowed plastic to become lodged between the door gasket, preventing the door from sealing properly. | 1 | Drain Blockage | 1CE4930A-3A33-4C49-A511-9497BD3477A9
CASE-0785 | Noticed black clamps was loose on left side of buffer box I secured both clamps by tightening. I poured new water into buffer box and Evac is calling and no water is dropping on clothing. | 1 | Drain Blockage | 946EBC80-B283-4F17-AFDE-104D05660CFC
CASE-0788 | I checked the isolation valves for the toilet and observed they were heavily corroded. In my professional opinion, I would not recommend trying to turn them off and would recommend shutting the water off at the main valve. | 1 | Valve Failure | C2E748F2-9EDC-4BC8-BCB1-43A2F80A46D8
CASE-0790 | Visible short with burnout noted on IC pathways. | 1 | Control Board Failure | 9CA630AB-8B9D-4002-BAD8-A03211FC054C
CASE-0762 | Digital assets asked I leak check with my electronic leak detector and if there is no leaks found to Located leak detector controllers and reset controllers. Found controllers and reset them. States changed from off to refrigeration and coolers are dropping temp and working properly at this time. | 1 | Control Board Failure | 202324D9-CA74-4CB3-8483-29EC01E7DA4A
CASE-0758 | Was already onsite found bakery freezer running at 16 degrees. Checked all pressures they are good. Liquid level is at 35%. Discharge air at evap is at -5. Freezer should come down to temp after hours due to rack failure | 1 | Rack Failure | ECDC4188-401E-402C-824A-E360E955B592
CASE-0794 | Noticed this new case shuts evaporator fans off once temperature set point has been reached. | 1 | Control Board Failure | A1E4E231-CB5A-4680-AA53-8ED83F945AE7
CASE-0737 | This tripped the low pressure fault, which requires a power cycle before the unit will run again. | 1 | Refrigerant Leak | E985A2EE-CFBD-4253-9322-C51242C62176
CASE-0727 | Found unit with product on it. Found it iced up. Adjusted it all the way to -9F. Adjusted parameters. TD was at 10 Adjusted it to 3 so at -9F it cuts out and cuts back in at -6F. | 1 | Control Board Failure | E42A26DF-FE02-4D6D-9BAA-C247D0403FC7
CASE-0731 | Repaired short going to auxiliary contact and system is no longer alarming. | 1 | Electrical Wiring | 519A1F47-85AD-4995-A8B8-31CCC7F5C98A
CASE-0732 | An oil sensor had a refrigerant leak and is being addressed on a different dispatch. | 1 | Refrigerant Leak | 6BC41CD2-9856-49BB-8371-D7B79B7F6945
CASE-0733 | Found suction EPR intermittently closing while solenoids were energized. Also found possible clogged distributor. Inefficient suction and liquid piping design for C1,C2, and C3 requiring protocol C to run near 7psi suction at all times to maintain temp on these cases. Quoting to reconfigure piping. | 1 | Piping Design Failure | 4A484642-A63C-439D-A5CD-EFF19748F3E3
CASE-0735 | Power unstable coming on then off then back on then stayed off again | 1 | Power Instability | 490793B6-5392-43F8-803F-AD83CE04413B
CASE-0736 | Seth verified that the low temp superheat is running at 30 and has been. | 1 | Refrigerant Leak | 0700430B-ECAA-46E2-A75F-CF07803D8ED1
CASE-0741 | Gaskets not repaired Still damaged | 1 | Gasket Failure | 1E49F77F-30C3-4F23-BE30-39F278C75063
CASE-0755 | Compressor is bad causing high temperature. | 1 | Compressor Failure | 9BDBF5BD-202D-49C6-8AEE-F929B9D30EED
CASE-0743 | Found unit had alarmed for EPR comm timeout. EPR board has no issues. Reset board and commanded EPR to open and close. EPR is responding and opening and closing properly. EPR is modulating properly at 1-8% and keeping unit at setpoint of 34F. | 1 | Control Board Failure | 41198516-2D82-4B9E-91B8-C4E00752C66B
CASE-0745 | WHILE ON-SITE, STORE POWER WENT OUT COMPLETELY. PERFORMED OPERATIONS CHECKS OF ALL REFRIGERATED EQUIPMENT, RACKS,CONDENSERS, ECT… ALL OK. NO ALARMS ON DEPARTURE | 1 | No Technical Fault | 27EFC4DD-CF6F-476F-B64F-1A6C5FD05749
CASE-0749 | I added CO2 until I got half a sight glass and the freezer went from 20 degrees to about 8 degrees | 1 | Refrigerant Leak | B39A271B-9719-4BAC-9E26-C0EB92540883
CASE-0751 | Found network home run behind B13 broken from poor install. | 1 | Electrical Wiring | 706B86B8-C3C5-40A5-89B7-3F09CEC6C411
CASE-0753 | Initial inspection found mechanical thermostat adjusted fully to the coldest setting. This operating condition would cause extended compressor run times, coil icing potential, unstable box temperatures, and product freezing symptoms previously reported. | 1 | Thermostat Failure | F4FDDEDE-45B9-4402-82F1-E4BBC6654F5D
CASE-0754 | Rack F High pressure alarm | 1 | No Technical Fault | 17B06080-A2E0-40AC-B449-B4C64114C57D
CASE-0792 | Found blower wheel clogged, cleaned blower wheel, noticeable increase in airflow | 1 | Fan Motor Failure | 5B527447-B8E4-4AB0-92B2-27698E18E24E
CASE-0797 | Removed defuser and closed off section that was blowing air to bakery display cases and adjusted air flow away from seafood self contained cooler. | 1 | Airflow Adjustment | C8867D96-D117-4F84-A507-5C45ADBCB0F3
CASE-0724 | Rack A no compressors running. No lights on electrical panel. 22 active alarms. | 1 | Compressor Failure | B72E0EE4-1CEA-4A2C-9D79-7CDD955A650D
CASE-0840 | There is no incoming power in the disconnect box. It is recommended to replace the motor | 1 | Electrical Wiring | 8B8C47B5-67CC-42ED-A60B-4D3D398F11D5
CASE-0831 | Found that liquid line size is 3/8s and checked manufacturer specs for lineset size and it should be 5/8s. | 1 | Line Size Mismatch | EAC6E1E3-E689-4444-B81F-F2842AD58CE6
CASE-0833 | Multiple Doors not closing properly. Need to replace Torque Rods | 1 | Mechanical Failure | 51FD3D47-D662-4A0E-BA2F-A23A10227300
CASE-0834 | Multiple Reach-in Freezer Door Gaskets Damaged. | 1 | Door Gasket Failure | 9E629AA6-EEB6-4D2C-AD6B-A673B07DDBF8
CASE-0836 | Found unit alarm for high pressure safety, running fan only. | 1 | High Pressure Alarm | 99605B98-9103-4613-8E57-488BEE8B5BE4
CASE-0837 | Idec Electronic Timer is in need of replacement. | 1 | Control Board Failure | AE30E8C5-6C06-47CA-BA40-DD7294C1A3EA
CASE-0839 | Found condensate pan unplugged from the unit. | 1 | Drain Blockage | 96DB9893-7254-4DB7-8399-CBD7AE222172
CASE-0842 | Compressor tear down and diag | 1 | Compressor Failure | 8DC98B20-AA69-44B4-B872-5B2467940CEF
CASE-0827 | tech then checked the bx controller and found store to be at dew point setpoint. | 1 | Control Board Failure | F381CB32-CB77-44D1-8582-DFDAA8C21E0F
CASE-0843 | Case currently at -2 degrees | 1 | Coil Failure | 7B178DC2-8024-453F-8559-C8A58960DBBF
CASE-0844 | Vfd for split condenser was causing liquid to stack in the condenser. Liquid is stacking on the split side of the condenser and not making its way back to the receiver. The controller sm880 says “bypass on fault” which is bypassing the vfd on the split side of the condenser. Not able to clear the fault since login is not high enough authority to make that change. Contacted Danfoss support to verify there was no faults with the vfd and they confirm vfd is running properly, issue is within the sm880. | 1 | Control Board Failure | 4913DBBF-C8FD-4699-B824-AE391042406C
CASE-0846 | found that leak is coming from plumbing supply lines ran through wall in area, there is a sink in seafood prep area, unable to gain access into wall to obtain visual on leak, and shutoff valves are at sink so shutoff to verify leak stops is not possible | 1 | Drain Blockage | 5694A630-B1C8-4E6E-9ECE-22E97B621E2E
CASE-0847 | Need to replace low temp compress lot 2 asap. Rack not making suction without it. Store went down with e2 failure overnight. | 1 | Compressor Failure | 681F2D5B-D2DD-4D9B-931B-0F6892FD331C
CASE-0849 | (2)-193426922 -CONTACTOR (1)-193443206- RELAY OVERLOAD 37A-50A (1)-193443103 16-25A RELAY OVERLOAD | 1 | Contactor Failure | CDADD9DF-94DA-47C4-82E5-EBB0050FA0BC
CASE-0850 | Pinpointed on aluminum u bend in back wall, appears rubbed out. | 1 | Refrigerant Leak | 94CE6CF9-0E87-4DD6-A4CE-C1291047DF3B
CASE-0828 | Arrived on site and checked in with manager, got into tire shop and proceeded to perform a maintenance on both portable ac units, cleaned condenser and evap coil filter screens, verified operations, and drained condensate drain reservoir. | 1 | Preventive Maintenance | 42E5752F-AAE0-47CB-B513-21AA52E74D9D
CASE-0826 | Open TXV and find TXV is almost fully stemmed out | 1 | TXV Failure | 5CE5B9AC-2E33-44FC-8147-BC8BCD7209EB
CASE-0798 | Call was created by HEB engineering to verify and change if necessary the condenser VFD parameter B1-02 set to 1. Verified both rack A and B were set this way. | 1 | Control Board Failure | CD38FE5F-CE52-44B7-8C58-31FE53998153
CASE-0809 | Found unit at 1* with set point of 27* | 1 | Control Board Failure | 516EBB08-2033-4801-BEBA-0EA25B09BCFC
CASE-0799 | REPLACE RIC FILTER DRIER - CLOGGED | 1 | Filter Drier Failure | FA5393F5-37B8-4C1F-92F8-6A5AB40F54D9
CASE-0800 | Found very small spot on the right side dripping water. Removed the old caulk from both sides and added new caulk. | 1 | Drain Blockage | 26C64A26-9263-433B-BEC9-E05A293D6395
CASE-0801 | After further trouble shooting we found that one of its safties are keeping it from running. I checked power to all of the safties and the only safety that was open was the high pressure control. There isn t a rest anywhere on it. With that being said it will need to be replaced because it will not close to where the comp will run. | 1 | High Pressure Switch Failure | 700F49D3-BC90-4CA0-AABC-6D768F003D99
CASE-0802 | Call not needed, tech fixed issue on 1-1831241 | 1 | No Technical Fault | EFF8D12A-9680-4575-8FFB-C404C63DB882
CASE-0803 | Arrived on site checked all salad bar pistons will need six total pistons ordered. Remove all bad pistons from salad bar and install new confirm that all glass is staying up on its own call complete | 1 | Piston Failure | C52D6885-EA92-49B0-A39D-65B7C998598A
CASE-0806 | Found condensing unit not running upon arrival. Off on high limit. Found intake grill covered with large label blocking the air intake. | 1 | Drain Blockage | B796180D-62AE-4C77-AE1F-3F21A22DFE47
CASE-0811 | Rack Proof alarm and b07 shows a WIB. | 1 | Control Board Failure | 14DDADAE-D5C0-4C06-9C6D-118580B081FE
CASE-0822 | It appears device absent alarm came on when he swapped it out | 1 | Control Board Failure | DCC478E5-79F1-4D2A-B5A3-B210C7B940E6
CASE-0812 | Logged into UltraSite, A + 20 fail failure fail and discharge fail | 1 | Control Board Failure | 01CAA1D8-4B52-4EC6-8621-D2F6B67C08AD
CASE-0813 | Logged Ultrasite, Rack A is in failure | 1 | Control Board Failure | 2BFB2AC5-AFF5-4199-BEFA-DC0138912101
CASE-0818 | Found terminal was broke off inside molex plug going to board. Found no voltage coming from board on S4 terminal. Found terminal was broke off inside molex plug going to board. Contacted Walmart Monitoring and they stated unit is in comms and running with no alarms besides Comp #1 HPS lockout. This call needs quoted. | 1 | Control Board Failure | D3EF21F4-F9AB-4FCA-97A6-B93821631A90
CASE-0819 | condenser coil temp sensor | 1 | Sensor Failure | F8ED6EC1-0B4C-4301-A7BA-05D8E868E11F
CASE-0820 | Rack B VFD compressor was in alarm. Contractor was pulled in. But pump wasn’t running. Noticed a lot of ice on all compressor End Bells. For medium temp compressors. As well as Accumulator. Tried power cycling VFD compressor. Pump would come on for a very short while then stop. Removed VFD cover. Noticed a lot of water. Dried up VFD. Removed water. Used a heat gun. Called up EMC and had them adjust SH target. From 3 degree target to 6 degrees. The ice started to melt. Reset compressor. It came on. Now drawing good amps. | 1 | Refrigerant Leak | BBD2AC56-C55B-4AA8-ACC9-B0143B02E796
CASE-0821 | Repaired dairy air door on WIC. | 1 | No Technical Fault | EB8E3D50-9328-4DAC-AC50-6DCC23CB21B7
CASE-0726 | Found Zero signs of fire. No notes no information . Went thru heat elements, adjusted belts and tested functions. No fires. Did notice fans noise but belt adjustment helped. Found no issues. | 1 | No Technical Fault | 11E58151-71EF-4B56-B602-7928A61F67D9
CASE-0720 | Unit operating at arrival, verified direct drive motor shut off and restarted multiple times. attached motor info. | 1 | No Technical Fault | 15CBE45F-9971-4622-A67A-445B54AF3606
CASE-0573 | UPON ARRIVAL MOD SHOWED TECH CASE RUNNING TO COLD. ADJUSTED SET POINT AND MONITORED TEMPS. CASE NOW RUNNING AT GOOD TEMPS AT THIS TIME | 1 | No Technical Fault | 752A324C-6465-4FA3-BBD1-8CCC0F884A9B
CASE-0644 | Found TXV adjusted TXV wouldn’t respond. | 1 | TXV Failure | EF78404A-4EE6-45A7-BCE5-77F5A220DFE1
CASE-0623 | Spoke with Greg on best way to shut off and powered unit down. Ensured that the other coil is running with no issues. | 1 | No Technical Fault | 605D8D6D-22F2-4992-97D9-18BBE4562579
CASE-0632 | Someone cleaned the exhaust hoods last night and left the exhaust hood disconnect off. The motor starter tripped because the hood was off. The bakery manager turned the exhaust fan back on at the fan. And reset the motor starter. Everything is running fine. Call is complete, caused from company who cleans exhaust hoods. | 1 | Electrical Wiring | D2A1ECD0-F9FD-4BFD-B45A-636822B37F2F
CASE-0637 | couldn't duplicate issue at this moment will return to further troubleshoot | 1 | No Technical Fault | BA74327E-39B3-427C-B2A9-344154FEB490
CASE-0639 | Found oil separator has been reading 16-17psi differential | 1 | Sensor Failure | D579DAE9-99CC-47F8-A657-C5F3699C5EF9
CASE-0641 | Trouble shot unit and case set for frozen. | 1 | Coil Failure | 13B32F96-78DA-492B-8139-265BA85753C2
CASE-0643 | Pulley bearing is very loud and has failed. Tstat not calling. Board still not comm with Gridpoint. | 1 | Sensor Failure | A8D460BA-9733-4587-A708-4BD7A0A859F7
CASE-0646 | Blast chiller LAE not working. Case does not seem level and is not allowing case to properly drain. This is allowing moisture over front lip and dripping on controller. | 1 | Drain Blockage | CA2F167F-76FB-40C8-97AB-1244CB1F9C7C
CASE-0619 | I found Burner 1 in Lockout mode. | 1 | Burner Lockout | FD2EE930-3C9F-49BF-B82A-C624D40C5891
CASE-0648 | Checked all contactors, fan blades, motor mounts, fuses. Everything looks good for the time being. | 1 | No Technical Fault | 3C4544AD-895A-42BF-B08E-7D5EF168EE8F
CASE-0649 | found on PM and just need to replace the TOP LEFT CONTACTOR ON RACK B | 1 | Contactor Failure | 6D9693AF-CD55-4613-8016-3193C362E4DC
CASE-0650 | we repaired a few leaks under the coffee bar and had to replace the faucet on the sink at the coffee bar. | 1 | Drain Blockage | BBCF8FF9-E23E-4BCD-A902-17EDB2353473
CASE-0653 | Check cooler condenser, unit has R22 refrigerant and site glass is still flashing after approximately 45 minutes of run time. | 1 | Refrigerant Leak | 17334A62-E0E1-431A-B766-9E35E3D5A5C6
CASE-0654 | Found that piping running to A04 is dripping water. Found that this circuit does not have ball valves to be isolated. Found most of frozen door aisle will need to be shut down as well as seafood reach in and bakery walk in. | 1 | Refrigerant Leak | A145D3F7-5222-4D0C-A74F-41E268EFBD61
CASE-0655 | Leak must be coming from mist system. | 1 | Mist System Failure | 8368B3D3-D829-44A5-8F23-6A8EB1940E68
CASE-0620 | Handle not functioning | 1 | Fan Motor Failure | FDABA3EA-8511-4BBD-9E94-A59C4BC08252
CASE-0618 | Found tower not over flowing or leaking water. Issue possibly related to water treatment sys. | 1 | Water Treatment System Failure | DD3778A6-26FF-4C74-AFD2-EE9CE6E8BC41
CASE-0659 | The EPR adjustment was made due to a whistling sound that we exercised out of the unit. | 1 | Valve Failure | CEED9592-F477-493A-A12C-1E62F7B21FAB
CASE-0590 | We will need to pump down circuit and change out EPR. | 1 | EPR Valve Failure | 64527F13-55CE-489F-A230-9DFE481E4CF3
CASE-0576 | Case did go into alarm on graph the 27th but has been fine every siince | 1 | No Technical Fault | CB557063-1294-4B7E-910B-4C9FD49B4822
CASE-0577 | error code 5 was showing, looked up and found that it was the airflow switch. Located and tested the switch, the switch was making a connection sometimes but not always. Removed the connections and added 2 new connectors. Switch now has a better connection and is no longer failing intermittently. After this unit turned on and noticed compressor sounded off like it was running in the wrong direction , switched the legs of power and compressor now spins the right way. | 1 | Airflow Switch Failure | 28B2D2FC-6580-4252-883A-D3975E0F0BFE
CASE-0580 | Removed mesh filter and observed temps lowered quicker and compressor would cycle off at setpoint, 34 degrees. During higher temps during the day, I would not recommend putting on the mesh filter because of case location and the load passing the load limit line. | 1 | Drain Blockage | FA58F104-6BC3-4B93-A30C-56867B836EDD
CASE-0581 | Found alarm cleared for high suction pressure. Found acorn in alarm. Fixed seal on valve above produce alarm cleared. | 1 | Refrigerant Leak | 6D3AA4F2-AD45-45F7-B59C-DCDB34EAF2C1
CASE-0584 | Klixon showing high ohms value when it should be open. Cut and capped termination wires. | 1 | Sensor Failure | 291038A6-3E41-4A4F-93CD-82CCE4893AD1
CASE-0586 | System had no pressure differential to push liquid to cases. | 1 | Refrigerant Leak | C2268B1D-6F56-4BED-82E2-FD0D5D91F703
CASE-0591 | Leak was found and asked MOD to create a new work order to perform repairs. | 1 | Refrigerant Leak | 6DCAC66C-7184-4EB2-85AC-81B94A3ACF52
CASE-0614 | Added gas to rack b on separate ticket | 1 | Refrigerant Leak | F0421106-9718-4FDD-8034-49A47DB3EEB8
CASE-0596 | Found TXV wide open, adjusted SH and evap was functioning normally. | 1 | TXV Failure | F21BD97F-5078-4B4F-AFC8-0786779DE629
CASE-0600 | Found back two cylinders full of oil. Removed oil and exercised pistons, found back two not moving which is causing compressor to become off balance and produce higher vibrations. | 1 | Compressor Failure | 1566B52D-B940-424F-94F8-F93499C8E520
CASE-0601 | On arrival box wasn’t alarming checked temp and box was telling around 10° graphed sensor and during the day there are a lot of spikes from door being left open. Verified coils weren’t iced up and all fans are running. Box pulls down to -3 during the night. | 1 | Sensor Failure | CD0C31AF-1F21-4A83-AC63-B17CC8EB149E
CASE-0606 | Found missing L3. | 1 | Electrical Wiring | 9C52515C-8353-4EF7-B974-1DB8845DB002
CASE-0611 | Changed MODBUS RTU enabled to on. Cleared alarm for water threshold. Changed parameters per Gunter tech support. Controller online. All fans running. No other problem found. | 1 | Control Board Failure | 9CDC4500-C1C4-4D28-AA99-48FA794DBCC4
CASE-0612 | The odor is strongest in anteroom and freezer 1. Inspected drain line piping and p trap had dried up indicating main plumbing and recent storm drains being the cause due to inclement weather. Added water to traps and smell was less pungent but still present. Issue is likely due to storms affecting main plumbing. The smell has gone away completely from inside the walk in freezers. I continued to check the drain lines and the drain pipes but they are all clear and there is no more smell at all. The freezers were not the cause of the smell what happened is that the odor got sucked into the freezers. This issue has been resolved there is no more ugly smell. | 1 | Drain Blockage | 64623A4A-71A4-43D0-A996-0646B09AF430
CASE-0658 | Found the drawer next to it was open. Checked and cooler was at setpoint. Cleaned off the fan guard and could feel the increase of air flow. Confirmed all drawers are closing correctly. | 1 | No Technical Fault | C268AF6E-E369-4603-B2E8-B689605E9EAC
CASE-0660 | the electrical cord attached to the freezer door is cracked and stripping from what looks like being shut in the door to many times | 1 | Electrical Wiring | 18AF7616-6497-431D-818B-8494ED819EB3
CASE-0719 | Replacing Deteriorating Evap Coil | 1 | Coil Failure | 31C54DF3-D351-4083-859E-038B59D071B4
CASE-0709 | No issue found, unit is running as programmed. I would leave this up to Jason if he wants to cost the first visit as a missed diagnosis since the tech didn't actually confirm the controller shut heat off and he didn't find the secondary tstat that actually controlls the system (outdated EMS) | 1 | No Technical Fault | 85CAF60E-E233-4D37-A23C-4337E046F9FC
CASE-0700 | Rack needs R134 a x120#.. | 1 | Refrigerant Leak | EC9F311F-5E18-4795-B229-F982C32577DD
CASE-0701 | High temp..slightly adjusted the sorit. Valve to lower temp. Also noted nobody in produce tonight,,,but every door wide open !!! | 1 | Drain Blockage | 99A9841D-AE8E-480E-AE51-021103D10466
CASE-0702 | Checked in with manager upon arrival. Gained access to rooftop rack C. Opened access doors to find refrigerant retrofit and oil change has already been completed after acid test failed. No oil change needed at this time. | 1 | No Technical Fault | CFF4AB04-B468-417F-983B-E2B7BB4A566F
CASE-0704 | Found damaged honeycomb/diffuser fell out and pulled off heater trim with it. | 1 | Coil Failure | B885D438-83CA-481F-9134-4922236B3EAB
CASE-0707 | PWIC (2) LED Light Fixtures out | 1 | LED Fixture Failure | 0FF2BF97-264C-401E-A29D-ED1404A6D109
CASE-0708 | Found a missing refrigeration cap inside the blower compartment and installed a new one. | 1 | Refrigerant Leak | 1FE0D34D-E2EC-4DF0-9B3F-88C7DC9CD6CE
CASE-0711 | The blade was hitting a rivet on the mount. I was able to adjust the motor/base so it’s no longer hitting anything. | 1 | Fan Motor Failure | 67F7A8A2-F701-4E63-A01C-8119DF5CE504
CASE-0698 | Rack A Oil Sample test fail (attached) | 1 | No Technical Fault | 065C2ED0-52D3-4195-927A-59C90C33FFDF
CASE-0712 | Rack 1 oldr rebuild kit oldr-16 unable to adjust and maintain a good differential Oldr rebuild kit older-16 unable to adjust and maintain a good differential Rack 4 needs a oldr16 rebuild unable to adjust and maintain a good differential | 1 | Refrigerant Leak | 1DA40AEC-FEB0-48BE-A5AA-2FEA928FF938
CASE-0713 | Doors tension came undone | 1 | Door Tension Failure | 2C5BCE6E-0203-467D-94E5-2F8396DC3BC0
CASE-0714 | Leak resolved nonissue found. | 1 | No Technical Fault | 4BFC875A-85E0-4124-A4B6-C5CEEAD0DD15
CASE-0716 | Compressor #5 not in alarm, and running properly. Oil was added to rack. Oil level is over 1st sight glass at reservoir. | 1 | Refrigerant Leak | BDF09168-3412-4DFF-9059-F88020B5BC2D
CASE-0717 | Replacing corroded Coils | 1 | Coil Failure | 44296902-29D9-4E56-91F3-8B9D13D354CE
CASE-0718 | I found heater splitting in several places. | 1 | Heater Failure | FD1E7F49-8800-4ED7-8F23-5A41C979DE94
CASE-0699 | Alarm cleared at arrival couodnt access evaps due to case being overstocked. Rack has some flash in glass. Suction and condenser pressures all good | 1 | No Technical Fault | 43AE1FA0-68F0-4D73-9EC0-9B6D939C1348
CASE-0695 | AHU at full capacity, running in 2nd stage; Heat reclaim valve bleeding and adding heat to store. Store Has dropped from 79° To 74° while onsite. | 1 | Valve Failure | A33671C0-4A3C-42CC-8C07-F909394F40B7
CASE-0661 | After checking out the power outlet found that it had power so pulled the back off the case and started checking it out. The back cover was dirty so cleaned it up and turned on the case. At this time the case came on and came down to temperature so asked the manager what temperature she wanted and she told me that the temperature the case was at was fine. | 1 | No Technical Fault | 7AF81AF7-C5C9-43CD-B6F9-604F6B298842
CASE-0680 | Found incorrect lines installed. | 1 | Electrical Wiring | AF6671EB-0A3D-450A-9AC6-DF66BD65BF44
CASE-0662 | The noise was gone and may have been caused by vibration from the liquid copper lines because of the water. | 1 | Drain Blockage | 59786718-F02D-441E-A816-C24A925E01A5
CASE-0664 | I arrived on-site and went to Rack D, located the produce prep cooler on the E3 (circuit D10), then contacted Seer2 and had them lower the setpoint from 40°F to 38°F; after letting the box run for a while, the E3 was reading 38°F and a direct temp check inside the box showed 39°F, confirming proper operation—job complete. | 1 | No Technical Fault | 70B7C7BD-C8BD-423A-AC1D-082352D11B05
CASE-0665 | Confirmed the rod on the assembly was cut too short | 1 | Mechanical Failure | E18E5EB5-5481-49FB-8146-9D26D9D51701
CASE-0672 | I then checked plug which was damaged. I then pulled new plug from van, DNI. I then installed new plug and checked operation. E2 is now operating properly and rack is now staying on and operating properly. | 1 | Electrical Wiring | B0F004BE-9302-4E05-AAED-E979A84CE12B
CASE-0674 | The AC setup is insufficient to provide comfort cooling to the office. | 1 | No Technical Fault | 554F5DBD-2C9E-4A26-9227-D3BD965474D2
CASE-0679 | Unit was shut off for a burning smell in the vestibule area. The case was found to be at the bottom of the elevator shaft. Not related the HVAC. Rtu4 is up and running, all setting back to auto | 1 | No Technical Fault | 492A3891-6B2C-4285-B15B-F92E915F0938
CASE-0681 | Found unloaded issue for both headers on C rack. | 1 | Coil Failure | 46FEFD11-A01A-4D5F-B62F-1112FF8B3D85
CASE-0692 | Made a couple little repairs in the WH | 1 | No Technical Fault | 5C5F387A-413B-4A81-998F-B017E8C4EEFA
CASE-0682 | One beep alarm points to over heating issue. And that hasn’t occurred. At all. | 1 | Sensor Failure | 71D7D929-90D8-4303-A07F-08268A118F57
CASE-0683 | Noticed unit very clogged with grease, grease buildup over blower, fan, and ductwork. All this grease buildup restricts proper airflow. This is also a major fire hazard. | 1 | Drain Blockage | 9D99012A-C142-4D8A-8EBC-1D69299038DB
CASE-0684 | Found both C1 and C2 off on run proof | 1 | Contactor Failure | F0AE879F-2935-4895-8A2C-65AD04801B92
CASE-0686 | Battery dead. | 1 | Electrical Wiring | 4209D97A-2DED-4C79-9F2B-D721F4798334
CASE-0688 | Box go down to 37, but went back up to 40. Employees are in and out of box non stop, with warm air from receiving coming in. | 1 | No Technical Fault | 0A70F5BD-7C37-4608-A00F-8E4290B96B86
CASE-0689 | Found the brass fitting that mount to the front of the compressor had some debris in that pick up port. Debris appears to be from the thread sealant from the factory. Used carb cleaner and clean fitting. Re installed and pulled vacuum. Repeated with master side and found this side worse. Cleaned and reinstalled. Turned unit back on and verified operations. | 1 | Oil Pressure Transducer Failure | E0C42756-E5F0-493B-AB57-BC6A16F70BAF
CASE-1186 | Found cap tube length at 155 inches talked with true who stated length should be 108 inches . | 1 | Cap Tube Failure | 9B670A82-583C-47FF-9A11-41D7842621F9